## DDC Schedule-BN-01
BMS
DDC PANEL SCHEDULE
SR. NO. | LEVEL | ZONE | PART | PANEL NAME | LOCATION | PANEL SIZE (H*W*D) | MOUNTING DETAIL | CANOPY | No. Of IO | Enclosure Installed | Panel Assembled | Remarks | DDC INSTALLATION | CABLE PULLING | PANEL TERMINATION | INSPECTIONS | REMARKS
1 | GF | Zone-4 | Part-3 | DDC-GF-01 | ELEC ROOM GF-293 | 800*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ |  |  |  | Pending containment in Zone-4
2 |  | Zone-4 | Part-1 | DDC-GF-02 | EQUIPMENT ROOM - GF-004 | 1000*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ |  |  |  | Pending containment in Zone-4
3 |  | Zone-1 | Part-2 | DDC-GF-03 | FCC ROOM - GF-108 | 1000*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ | ✔️ | ✔️
4 |  | Zone-2 | Part-3 | DDC-GF-04 | STORAGE ROOM - GF-074 | 800*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ | ✔️
5 |  | Zone-3 | Part-2 | DDC-GF-05 | ELEC ROOM - GF-315 | 800*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ | ✔️ | ✔️
6 | FF | Zone-3 | Part-3 | DDC-FF-01 | FIRST FLOOR - ZONE 3 PART 3 - ELEC ROOM | 800*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ | ✔️ | ✔️
7 |  | Zone-2 | Part-3 | DDC-FF-02 | FIRST FLOOR - ZONE2 PART 3 - ELEC ROOM | 800*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ | ✔️
8 | SF | Zone-4 | Roof | DDC-SF-01 | SECOND FLOOR - ZONE 4 ROOF | 1000*800*250 | WALL MOUNT | REQUIRED |  | ✔️ | ✔️ | [5 empty] | Awaiting I/O List confirmation for panel fabrication
9 |  | Zone-1 | Roof | DDC-SF-02 | SECOND FLOOR - ZONE 1 ROOF | 800*800*250 | WALL MOUNT | REQUIRED |  | ✔️ | ✔️ | Half assembled. Modification required |  |  |  |  | Awaiting workfront access
10 | RF | Zone-3 | Part-1 | DDC-RF-01 | ROOF FLOOR - ZONE 3 PART 1 ROOF-ELEC ROOM | 1000*1000*300 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ | ✔️ |  |  | Awaiting workfront access
11 |  | Zone-2 | Part-1 | DDC-RF-02 | ROOF FLOOR - ZONE 2 PART 1 ROOF - PUMP ROOM | 800*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ | Half assembled. Modification required | ✔️ |  |  |  | Awaiting workfront access
12 |  | Zone-3 | Part-1 | DDC-RF-03 | ROOF FLOOR - ZONE 3 PART 1 ROOF - GSM ROOM | 800*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ |  |  |  | Awaiting workfront access
13 |  | Zone-2 | Part-3 | DDC-RF-04 | ROOF FLOOR - ZONE 2 PART 3 ROOF-ELEC ROOM | 1000*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ |  | ✔️ |  |  |  | Awaiting workfront access
14 |  | Zone-3 | Part-3 | DDC-RF-05 | ROOF FLOOR - ZONE 3 PART 3 ROOF- PUMP ROOM | 800*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ | Half assembled. Modification required | ✔️ |  |  |  | Awaiting workfront access
15 | SWP PUMP ROOM |  |  | DDC-SP-01 | SWIMMING POOL PUMP ROOM | 600*600*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ | Not assembled |  |  |  |  | Awaiting workfront access
16 | SUBSTATION |  |  | DDC-SB-01 | LV ROOM - SUBSTATION | 1000*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ | Panel assembled. Enclosure not delivered |  |  |  |  | Awaiting workfront access
17 | PARKING LOWER LEVEL |  |  | DDC-LG-01 | PARKING LOWER GROUND PUMP ROOM | 1000*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ | Half assembled. Modification required |  |  |  |  | Awaiting workfront access
18 |  |  |  | DDC-LG-02 | PARKING LOWER GROUND ELECTRICAL ROOM | 1000*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️ | [5 empty] | Awaiting I/O List confirmation for panel fabrication
19 |  |  |  | DDC-LG-03 | PARKING LOWER GROUND ELECTRICAL ROOM | 1000*800*250 | WALL MOUNT | N/A |  | ✔️ | ✔️
20 | PARKING UPPER LEVEL |  |  | DDC-UG-01 | PARKING UPPER GROUND ELECTRICAL ROOM | 1000*800*250 | WALL MOUNT | N/A |  | ✔️ | ❌ | Not assembled |  |  |  |  | Awaiting I/O List confirmation for panel fabrication
21 |  |  |  | DDC-UG-02 | PARKING UPPER GROUND ELECTRICAL ROOM | 1000*800*250 | WALL MOUNT | N/A |  | ✔️ | ❌ | Not assembled

## DDC-GF-01
DDC-GF-01
Project - BN-01 DDC SIZE - 800 * 800 DDC IP - BACNET ID - 900
Controller-DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | CAHU-GF-04 | Supply Fan Start/Stop Command | BO-1 | R1 | CAHU4-Start/Stop Command | MCC
| UO2 |  | CAHU-GF-05 | Supply Fan Start/Stop Command | BO-2 | R2 | CAHU5-Start/Stop Command | MCC
| UO3 | GND | CAHU-GF-06 | Supply Fan Start/Stop Command | BO-3 | R3 | CAHU6-Start/Stop Command | MCC
| UO4 |  |  | SPARE
| UO5 | GND | CAHU-GF-04 | CHW Valve Control Signal | AO-5 | 4 | CAHU4- CHW CMD | ACTUATOR
| UO6 |  | CAHU-GF-05 | CHW Valve Control Signal | AO-6 | 5 | CAHU5- CHW CMD | ACTUATOR
| UO7 | GND | CAHU-GF-06 | CHW Valve Control Signal | AO-7 | 6 | CAHU6- CHW CMD | ACTUATOR
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | CAHU-GF-04 | Space Temperature | AI-3 | 7 | CAHU4-Space Temp | SENSOR
| UI4 |  | CAHU-GF-04 | CHW Feedback | AI-4 | 8 | CAHU4-CHW Feedback | ACTUATOR
| UI5 | GND | CAHU-GF-04 | CHW Return Temp | AI-5 | 9 | CAHU4- CHW Ret Temp. | SENSOR
| UI6 |  | CAHU-GF-05 | Space Temperature | AI-6 | 10 | CAHU5-Space Temp | SENSOR
| UI7 | GND | CAHU-GF-05 | CHW Feedback | AI-7 | 11 | CAHU5-CHW Feedback | ACTUATOR
| UI8 |  | CAHU-GF-05 | CHW Return Temp | AI-8 | 12 | CAHU5- CHW Ret Temp. | SENSOR
| UI9 | GND | CAHU-GF-06 | Space Temperature | AI-9 | 13 | CAHU6-Space Temp | SENSOR
| UI10 |  | CAHU-GF-06 | CHW Feedback | AI-10 | 14 | CAHU6-CHW Feedback | ACTUATOR
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | CAHU-GF-06 | CHW Return Temp | AI-43 | 15 | CAHU6- CHW Ret Temp. | SENSOR
| UI2 |  |  | SPARE
| UI3 | GND | CAHU-GF-04 | Supply Fan Auto Status | BI-45 | 16 | CAHU4- SF Auto Sts | MCC
| UI4 |  | CAHU-GF-04 | Supply Fan Run Status | BI-46 | 17 | CAHU4- SF Run Sts | MCC
| UI5 | GND | CAHU-GF-04 | Supply Fan Trip Status | BI-47 | 18 | CAHU4- SF Trip Sts | MCC
| UI6 |  | CAHU-GF-04 | Supply Fan Flow Status | BI-48 | 19 | CAHU4- SF Flow Sts | SWITCH
| UI7 | GND | CAHU-GF-05 | Supply Fan Auto Status | BI-49 | 20 | CAHU5- SF Auto Sts | MCC
| UI8 |  | CAHU-GF-05 | Supply Fan Run Status | BI-50 | 21 | CAHU5- SF Run Sts | MCC
| UI9 | GND | CAHU-GF-05 | Supply Fan Trip Status | BI-51 | 22 | CAHU5- SF Trip Sts | MCC
| UI10 |  | CAHU-GF-05 | Supply Fan Flow Status | BI-52 | 23 | CAHU5- SF Flow Sts | SWITCH
| UI11 | GND | CAHU-GF-06 | Supply Fan Auto Status | BI-53 | 24 | CAHU6- SF Auto Sts | MCC
| UI12 |  | CAHU-GF-06 | Supply Fan Run Status | BI-54 | 25 | CAHU6- SF Run Sts | MCC
| UI13 | GND | CAHU-GF-06 | Supply Fan Trip Status | BI-55 | 26 | CAHU6- SF Trip Sts | MCC
| UI14 |  | CAHU-GF-06 | Supply Fan Flow Status | BI-56 | 27 | CAHU6- SF Flow Sts | SWITCH
| UI15 | GND | SMDB-GF-MP | Incomer Breaker Run | BI-57 | 28 | SMDB-GF-MP- Breaker Run | MCC | EL-RM GF-293
| UI16 |  | SMDB-GF-MP | Incomer Breaker Trip | BI-58 | 29 | SMDB-GF-MP- Breaker Trip | MCC | EL-RM GF-293
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | ESMDB-GF-MP | Incomer Breaker Run | BI-59 | 30 | ESMDB-GF-MP- Breaker Run | MCC | EL-RM GF-293
| UI2 |  | ESMDB-GF-MP | Incomer Breaker Trip | BI-60 | 31 | ESMDB-GF-MP- Breaker Trip | MCC | EL-RM GF-293
| UI3 | GND | SMDB | Incomer Breaker Run | BI-61 | 32 | SMDB- Breaker Run | MCC | EL-RM GF-293
| UI4 |  | SMDB | Incomer Breaker Trip | BI-62 | 33 | SMDB- Breaker Trip | MCC | EL-RM GF-293
| UI5 | GND | GATE BARRIER-1 | On/Off Status | BI-63 | 34 | GB1- On/Off Sts | MCC
| UI6 |  | GATE BARRIER-2 | On/Off Status | BI-64 | 35 | GB2- On/Off Sts | MCC
| UI7 | GND | Leak Detection System-1 | Leak Alarm | BI-65 | 36 | OLDS - Leak Alarm | MCC | EL-RM GF-293
| UI8 |  |  | SPARE
| UI9 | GND |  | SPARE
| UI10 |  |  | SPARE
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-GF-02
DDC-GF-02
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - 901
Controller-DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | CAHU-GF-01 | Supply Fan Start/Stop Command | BO-1 | R1 | CAHU1-Start/Stop Command | MCC
| UO2 |  | CAHU-GF-02 | Supply Fan Start/Stop Command | BO-2 | R2 | CAHU2-Start/Stop Command | MCC
| UO3 | GND | CAHU-GF-03 | Supply Fan Start/Stop Command | BO-3 | R3 | CAHU3-Start/Stop Command | MCC
| UO4 |  | DX-UNIT-1 | Enable/Disable Command | BO-4 | R4 | DX1 -Start/Stop Command | MCC
| UO5 | GND | DX-UNIT-2 | Enable/Disable Command | BO-5 | R5 | DX2 -Start/Stop Command | MCC
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | CAHU-GF-01 | Space Temperature | AI-3 | 6 | CAHU1-Space Temp | SENSOR
| UI4 |  | CAHU-GF-01 | CHW Feedback | AI-4 | 7 | CAHU1-CHW Feedback | ACTUATOR
| UI5 | GND | CAHU-GF-01 | CHW Return Temp | AI-5 | 8 | CAHU1- CHW Ret Temp. | SENSOR
| UI6 |  | CAHU-GF-02 | Space Temperature | AI-6 | 9 | CAHU2-Space Temp | SENSOR
| UI7 | GND | CAHU-GF-02 | CHW Feedback | AI-7 | 10 | CAHU2-CHW Feedback | ACTUATOR
| UI8 |  | CAHU-GF-02 | CHW Return Temp | AI-8 | 11 | CAHU2- CHW Ret Temp. | SENSOR
| UI9 | GND | CAHU-GF-03 | Space Temperature | AI-9 | 12 | CAHU3-Space Temp | SENSOR
| UI10 |  | CAHU-GF-03 | CHW Feedback | AI-10 | 13 | CAHU3-CHW Feedback | ACTUATOR
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | CAHU-GF-01 | CHW Valve Control Signal | AO-9 | 14 | CAHU1- CHW CMD | ACTUATOR
| UO2 |  | CAHU-GF-02 | CHW Valve Control Signal | AO-10 | 15 | CAHU2- CHW CMD | ACTUATOR
| UO3 | GND | CAHU-GF-03 | CHW Valve Control Signal | AO-11 | 16 | CAHU3- CHW CMD | ACTUATOR
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE NUMBER TERM SIDE | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | CAHU-GF-03 | CHW Return Temp | AI-11 | 17 | CAHU3- CHW Ret Temp. | SENSOR
| UI2 |  | DX-UNIT-1 | Space Temperature | AI-12 | 18 | DX1- Space Temp. | SENSOR
| UI3 | GND | DX-UNIT-2 | Space Temperature | AI-13 | 19 | DX2- Space Temp. | SENSOR
| UI4 |  |  | SPARE
| UI5 | GND | DX-UNIT-1 | Unit On/Off Status | BI-15 | 20 | DX1- Unit On/Off Sts | MCC
| UI6 |  | DX-UNIT-2 | Unit On/Off Status | BI-16 | 21 | DX2- Unit On/Off Sts | MCC
| UI7 | GND | PAVA-1 | On/Off Status | BI-17 | 22 | PAVA- On/Off Sts | MCC | Security Equipment Room -004
| UI8 |  | PAVA-1 | Common Fault | BI-18 | 23 | PAVA- Common Fault Sts | MCC | Security Equipment Room -004
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | CAHU-GF-01 | Supply Fan Auto Status | BI-59 | 24 | CAHU1- SF Auto Sts | MCC
| UI2 |  | CAHU-GF-01 | Supply Fan Run Status | BI-60 | 25 | CAHU1- SF Run Sts | MCC
| UI3 | GND | CAHU-GF-01 | Supply Fan Trip Status | BI-61 | 26 | CAHU1- SF Trip Sts | MCC
| UI4 |  | CAHU-GF-01 | Supply Fan Flow Status | BI-62 | 27 | CAHU1- SF Flow Sts | SWITCH
| UI5 | GND | CAHU-GF-02 | Supply Fan Auto Status | BI-63 | 28 | CAHU2- SF Auto Sts | MCC
| UI6 |  | CAHU-GF-02 | Supply Fan Run Status | BI-64 | 29 | CAHU2- SF Run Sts | MCC
| UI7 | GND | CAHU-GF-02 | Supply Fan Trip Status | BI-65 | 30 | CAHU2- SF Trip Sts | MCC
| UI8 |  | CAHU-GF-02 | Supply Fan Flow Status | BI-66 | 31 | CAHU2- SF Flow Sts | SWITCH
| UI9 | GND | CAHU-GF-03 | Supply Fan Auto Status | BI-67 | 32 | CAHU3- SF Auto Sts | MCC
| UI10 |  | CAHU-GF-03 | Supply Fan Run Status | BI-68 | 33 | CAHU3- SF Run Sts | MCC
| UI11 | GND | CAHU-GF-03 | Supply Fan Trip Status | BI-69 | 34 | CAHU3- SF Trip Sts | MCC
| UI12 |  | CAHU-GF-03 | Supply Fan Flow Status | BI-70 | 35 | CAHU3- SF Flow Sts | SWITCH
| UI13 | GND | CCTV-1 | On/Off Status | BI-71 | 36 | CCTV1- On/Off Sts | MCC | Security Equipment Room -004
| UI14 |  | CCTV-1 | Fault Status | BI-72 | 37 | CCTV1- Fault Sts | MCC | Security Equipment Room -004
| UI15 | GND | CCTV-2 | On/Off Status | BI-73 | 38 | CCTV2- On/Off Sts | MCC | Security Equipment Room -004
| UI16 |  | CCTV-2 | Fault Status | BI-74 | 39 | CCTV2- Fault Sts | MCC | Security Equipment Room -004
| 24VAC | ~
0VAC

## DDC-GF-03
DDC-GF-03
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - 903
Controller-DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | DX-UNIT-3 | Enable/Disable Command | BO-1 | R1 | DX3 -Start/Stop Command | MCC
| UO2 |  |  | SPARE
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | DX-UNIT-3 | Space Temperature | AI-3 | 2 | DX3- Space Temp. | SENSOR
| UI4 |  | HRAHU -RF-03 | Space Temperature | AI-4 | 3 | HRAHU-RF3- Space Temp. | SENSOR
| UI5 | GND | HRAHU-RF-06 | Space Temperature | AI-5 | 4 | HRAHU-RF3- Space Temp. | SENSOR
| UI6 |  |  | SPARE
| UI7 | GND | DX-UNIT-3 | Unit On/Off Status | BI-7 | 5 | DX3- Unit On/Off Sts | MCC
| UI8 |  | SMDB-EV-EXT | Incomer Breaker Run | BI-8 | 6 | SMDB-EV-EXT- Breaker Run | MCC | EL RM GF-107
| UI9 | GND | SMDB-EV-EXT | Incomer Breaker Trip | BI-9 | 7 | SMDB-EV-EXT- Breaker Trip | MCC | EL RM GF-107
| UI10 |  | TDA SERVER-1 | Unit On/Off Status | BI-10 | 8 | TDA1- On/Off Sts | MCC | FCC ROOM
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | TDA SERVER-1 | Common Fault | BI-43 | 17 | TDA1- Fault Sts | MCC | FCC ROOM
| UI2 |  | PAVA-2 | On/Off Status | BI-44 | 18 | PAVA2- On/Off Sts | MCC | FCC ROOM
| UI3 | GND | PAVA-2 | Common Fault | BI-45 | 19 | PAVA2- Common Fault Sts | MCC | FCC ROOM
| UI4 |  | GATE BARRIER-4 | On/Off Status | BI-46 | 20 | GB4- On/Off Sts | MCC
| UI5 | GND | GATE BARRIER-5 | On/Off Status | BI-47 | 21 | GB5- On/Off Sts | MCC
| UI6 |  | GATE BARRIER-6 | On/Off Status | BI-48 | 22 | GB6- On/Off Sts | MCC
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| UI9 | GND |  | SPARE
| UI10 |  |  | SPARE
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-GF-04
DDC-GF-04
Project - BN-01 DDC SIZE - 800 * 800 DDC IP - BACNET ID - 904
Controller-DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND |  | SPARE
| UO2 |  |  | SPARE
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | HRAHU -RF-02 | Space Temperature | AI-3 | 1 | HRAHU-RF2- Space Temp. | SENSOR
| UI4 |  |  | SPARE
| UI5 | GND | SMDB-GF-4 | Incomer Breaker Run | BI-5 | 2 | SMDB-GF-4- Breaker Run | MCC | EL RM GF-083
| UI6 |  | SMDB-GF-4 | Incomer Breaker Trip | BI-6 | 3 | SMDB-GF-4- Breaker Trip | MCC | EL RM GF-083
| UI7 | GND | ESMDB-GF-4 | Incomer Breaker Run | BI-7 | 4 | ESMDB-GF-4- Breaker Run | MCC | EL RM GF-083
| UI8 |  | ESMDB-GF-4 | Incomer Breaker Trip | BI-8 | 5 | ESMDB-GF-4- Breaker Trip | MCC | EL RM GF-083
| UI9 | GND | AIR CURTAIN-1 | On/Off Status | BI-9 | 6 | AC6- On/Off Status | MCC
| UI10 |  | AIR CURTAIN-2 | On/Off Status | BI-10 | 7 | AC7- On/Off Status | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | LIFT-4 | Run Status | BI-43 | 8 | LIFT2- Run Sts | MCC
| UI2 |  | LIFT-4 | Fault Status | BI-44 | 9 | LIFT2- Fault Sts | MCC
| UI3 | GND | LIFT-4 | Cabin Fault Alarm | BI-45 | 10 | LIFT2- Cabin Fault Alarm | MCC
UI4
| UI5 | GND
UI6
| UI7 | GND
UI8
| UI9 | GND
UI10
| UI11 | GND
UI12
| UI13 | GND
UI14
| UI15 | GND
UI16
| 24VAC | ~
0VAC

## DDC-GF-05
DDC-GF-05
Project - BN-01 DDC SIZE - 800 * 800 DDC IP - BACNET ID -
Controller-DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | DX-UNIT-4 | Enable/Disable Command | BO-1 | R1 | DX4 -Start/Stop Command | MCC
| UO2 |  | DX-UNIT-5 | Enable/Disable Command | BO-2 | R2 | DX5 -Start/Stop Command | MCC
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | UPS ROOM | Space Temperature | AI-3 | 3 | UPS ROOM- Space Temp. | SENSOR
| UI4 |  | ELECTRICAL ROOM | Space Temperature | AI-4 | 4 | ELE ROOM- Space Temp. | SENSOR
| UI5 | GND | CORRIDOR | Space Temperature | AI-5 | 5 | CORRIDOR- Space Temp. | SENSOR
| UI6 |  | DX-UNIT-4 | Space Temperature | AI-6 | 6 | DX4- Space Temp. | SENSOR
| UI7 | GND | DX-UNIT-5 | Space Temperature | AI-7 | 7 | DX5- Space Temp. | SENSOR
| UI8 |  |  | SPARE
| UI9 | GND | DX-UNIT-4 | Unit On/Off Status | BI-9 | 8 | DX4- Unit On/Off Sts | MCC
| UI10 |  | DX-UNIT-5 | Unit On/Off Status | BI-10 | 9 | DX5- Unit On/Off Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | Leak Detection System-2 | Leak Alarm | BI-43 | 10 | Leak Alarm | SENSOR | SERVER RM GF-020
| UI2 |  | MCS-1 | On/Off Status | BI-44 | 11 | MCS1- On/Off Sts | MCC | SERVER RM GF-020
| UI3 | GND | MCS-1 | Common Fault | BI-45 | 12 | MCS1- Fault Sts | MCC | SERVER RM GF-020
| UI4 |  | MCS-2 | On/Off Status | BI-46 | 13 | MCS2- On/Off Sts | MCC | SERVER RM GF-020
| UI5 | GND | MCS-2 | Common Fault | BI-47 | 14 | MCS2- Fault Sts | MCC | SERVER RM GF-020
| UI6 |  | SMDB-GF-1 | Incomer Breaker Run | BI-48 | 15 | SMDB-GF1- Breaker Run | MCC | EL RM GF-315
| UI7 | GND | SMDB-GF-1 | Incomer Breaker Trip | BI-49 | 16 | SMDB-GF1- Breaker Trip | MCC | EL RM GF-315
| UI8 |  | ESMDB-GF-1 | Incomer Breaker Run | BI-50 | 17 | ESMDB-GF1- Breaker Run | MCC | EL RM GF-315
| UI9 | GND | ESMDB-GF-1 | Incomer Breaker Trip | BI-51 | 18 | ESMDB-GF1- Breaker Trip | MCC | EL RM GF-315
| UI10 |  | USMDB-GF-1 | Incomer Breaker Run | BI-52 | 19 | USMDB-GF1- Breaker Run | MCC | EL RM GF-315
| UI11 | GND | USMDB-GF-1 | Incomer Breaker Trip | BI-53 | 20 | USMDB-GF1- Breaker Trip | MCC | EL RM GF-315
| UI12 |  | SMDB-FF-1 | Incomer Breaker Run | BI-54 | 21 | SMDB-FF1- Breaker Run | MCC | EL RM GF-315
| UI13 | GND | SMDB-FF-1 | Incomer Breaker Trip | BI-55 | 22 | SMDB-FF1- Breaker Trip | MCC | EL RM GF-315
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-FF-01
DDC-FF-01
Project - BN-01 DDC SIZE - 800 * 800 DDC IP - BACNET ID -
Controller-DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND |  | SPARE
| UO2 |  |  | SPARE
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | SMDB-GF-2 | Incomer Breaker Run | BI-3 | 1 | SMDB-GF-2- Breaker Run | MCC | EL RM GF-284
| UI4 |  | SMDB-GF-2 | Incomer Breaker Trip | BI-4 | 2 | SMDB-GF-2- Breaker Trip | MCC | EL RM GF-284
| UI5 | GND | ESMDB-GF-2 | Incomer Breaker Run | BI-5 | 3 | ESMDB-GF-2- Breaker Run | MCC | EL RM GF-284
| UI6 |  | ESMDB-GF-2 | Incomer Breaker Trip | BI-6 | 4 | ESMDB-GF-2- Breaker Trip | MCC | EL RM GF-284
| UI7 | GND | SMDB-FF-2 | Incomer Breaker Run | BI-7 | 5 | SMDB-FF-2- Breaker Run | MCC | EL RM FF-144
| UI8 |  | SMDB-FF-2 | Incomer Breaker Trip | BI-8 | 6 | SMDB-FF-2- Breaker Trip | MCC | EL RM FF-144
| UI9 | GND | SMDB-SF-2 | Incomer Breaker Run | BI-9 | 7 | SMDB-SF-2- Breaker Run | MCC | EL RM SF-160
| UI10 |  | SMDB-SF-2 | Incomer Breaker Trip | BI-10 | 8 | SMDB-SF-2- Breaker Trip | MCC | EL RM SF-160
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | LIFT-2 | Run Status | BI-43 | 9 | LIFT2- Run Sts | MCC
| UI2 |  | LIFT-2 | Fault Status | BI-44 | 10 | LIFT2- Fault Sts | MCC
| UI3 | GND | LIFT-2 | Cabin Fault Alarm | BI-45 | 11 | LIFT2- Cabin Fault Alarm | MCC
| UI4 |  |  | SPARE
| UI5 | GND |  | SPARE
| UI6 |  |  | SPARE
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| UI9 | GND |  | SPARE
| UI10 |  |  | SPARE
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-FF-02
DDC-FF-02
Project - BN-01 DDC SIZE - 800 * 800 DDC IP - BACNET ID -
Controller-DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND |  | SPARE
| UO2 |  |  | SPARE
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | HRAHU -RF-04 | Space Temperature | AI-3 | 1 | HRAHU-RF04- Space Temp | SENSOR
| UI4 |  |  | SPARE
| UI5 | GND | SMDB-GF-3 | Incomer Breaker Run | BI-5 | 2 | SMDB-GF3- Breaker Run | MCC | EL RM GF-154
| UI6 |  | SMDB-GF-3 | Incomer Breaker Trip | BI-6 | 3 | SMDB-GF3- Breaker Trip | MCC | EL RM GF-154
| UI7 | GND | ESMDB-GF-3 | Incomer Breaker Run | BI-7 | 4 | ESMDB-GF3- Breaker Run | MCC | EL RM GF-154
| UI8 |  | ESMDB-GF-3 | Incomer Breaker Trip | BI-8 | 5 | ESMDB-GF3- Breaker Trip | MCC | EL RM GF-154
| UI9 | GND | AIR CURTAIN-3 | On/Off Status | BI-9 | 6 | Air-Curtain-3- ON/OFF Sts | MCC
| UI10 |  | AIR CURTAIN-4 | On/Off Status | BI-10 | 7 | Air-Curtain-4- ON/OFF Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | AIR CURTAIN-5 | On/Off Status | BI-43 | 8 | Air-Curtain-5- ON/OFF Sts | MCC
| UI2 |  | GATE BARRIER-7 | On/Off Status | BI-44 | 9 | Gate-Barrier-7- ON/OFF Sts | MCC
| UI3 | GND | GATE BARRIER-8 | On/Off Status | BI-45 | 10 | Gate-Barrier-8- ON/OFF Sts | MCC
| UI4 |  | SMDB-FF-3 | Incomer Breaker Run | BI-46 | 11 | SMDB-FF3- Breaker Run | MCC | EL ROOM - FF-084
| UI5 | GND | SMDB-FF-3 | Incomer Breaker Trip | BI-47 | 12 | SMDB-FF3- Breaker Trip | MCC | EL ROOM - FF-084
| UI6 |  |  | SPARE
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| UI9 | GND |  | SPARE
| UI10 |  |  | SPARE
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-SF-01
DDC-SF-01
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | AHU-SF-01-GYM | Supply Fan Start/Stop Command | BO-1 | R1 | AHU-GYM- SF Start/Stop Cmd | MCC
| UO2 |  | AHU-SF-01-GYM | Exhaust Fan Start/Stop Command | BO-2 | R2 | AHU-GYM- EF Start/Stop Cmd | MCC
| UO3 | GND | AHU-SF-01-GYM | HRW Start/Stop Command | BO-3 | R3 | AHU-GYM- HRW Cmd | MCC
| UO4 |  | AHU-SF-02-SWP | Supply Fan Start/Stop Command | BO-4 | R4 | AHU-SWP- SF Start/Stop Cmd | MCC
| UO5 | GND | AHU-SF-02-SWP | Exhaust Fan Start/Stop Command | BO-5 | R5 | AHU-SWP- EF Start/Stop Cmd | MCC
| UO6 |  | AHU-SF-02-SWP | HRW Start/Stop Command | BO-6 | R6 | AHU-SWP- HRW Cmd | MCC
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | AHU-SF-01-GYM | Supply Fan ON/OFF Status | BI-3 | 7 | AHU-GYM- SF ON/OFF Sts | MCC
| UI4 |  | AHU-SF-01-GYM | Supply Fan Trip Status | BI-4 | 8 | AHU-GYM- SF Trip Sts | MCC
| UI5 | GND | AHU-SF-01-GYM | Supply Fan Auto Position | BI-5 | 9 | AHU-GYM- SF Auto Sts | MCC
| UI6 |  | AHU-SF-01-GYM | Supply Fan Proof of Flow | BI-6 | 10 | AHU-GYM- SF Flow Sts | SWITCH
| UI7 | GND | AHU-SF-01-GYM | Exhaust Fan ON/OFF Status | BI-7 | 11 | AHU-GYM- EF ON/OFF Sts | MCC
| UI8 |  | AHU-SF-01-GYM | Exhaust Fan Trip Status | BI-8 | 12 | AHU-GYM- EF Trip Sts | MCC
| UI9 | GND | AHU-SF-01-GYM | Exhaust Fan Auto Position | BI-9 | 13 | AHU-GYM- EF Auto Sts | MCC
| UI10 |  | AHU-SF-01-GYM | Exhaust Fan Proof of Flow | BI-10 | 14 | AHU-GYM- EF Flow Sts | SWITCH
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | AHU-SF-01-GYM | Supply Fan VFD Control Signal | AO-9 | 15 | AHU-GYM- SF VFD CMD | VFD
| UO2 |  | AHU-SF-01-GYM | CHW Valve Control Signal | AO-10 | 16 | AHU-GYM- CHW CMD | ACTUATOR
| UO3 | GND | AHU-SF-01-GYM | Exhaust Fan VFD Control Signal | AO-11 | 17 | AHU-GYM- EF VFD CMD | VFD
| UO4 |  | AHU-SF-01-GYM | Reheat Valve Control Signal | AO-12 | 18 | AHU-GYM- Reheat CMD | ACTUATOR
| UO5 | GND | AHU-SF-02-SWP | Supply Fan VFD Control Signal | AO-13 | 19 | AHU-SWP- SF VFD CMD | VFD
| UO6 |  | AHU-SF-02-SWP | CHW Valve Control Signal | AO-14 | 20 | AHU-SWP- CHW CMD | ACTUATOR
| UO7 | GND | AHU-SF-02-SWP | Exhaust Fan VFD Control Signal | AO-15 | 21 | AHU-SWP- EF VFD CMD | VFD
| UO8 |  | AHU-SF-02-SWP | Reheat Valve Control Signal | AO-16 | 22 | AHU-SWP- Reheat CMD | ACTUATOR
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | AHU-SF-01-GYM | Fresh Air Damper Open/Close Status | BI-11 | 23 | AHU-GYM- FA Damper Sts | SWITCH
| UI2 |  | AHU-SF-01-GYM | Return Air Damper Open/Close Status | BI-12 | 24 | AHU-GYM- RA Damper Sts | SWITCH
| UI3 | GND | AHU-SF-01-GYM | Exhaust Air Damper Open/Close Status | BI-13 | 25 | AHU-GYM- EA Damper Sts | SWITCH
| UI4 |  | AHU-SF-01-GYM | Pre-Filter Dirty Status | BI-14 | 26 | AHU-GYM- Pre Filter Dirty | SWITCH
| UI5 | GND | AHU-SF-01-GYM | Bag Filter Dirty Status | BI-15 | 27 | AHU-GYM- Bag Filter Dirty | SWITCH
| UI6 |  | AHU-SF-01-GYM | Total Recovery Wheel ON/OFF Status | BI-16 | 28 | AHU-GYM- HRW ON/OFF Sts | MCC
| UI7 | GND | AHU-SF-01-GYM | Total Recovery Wheel Fault Status | BI-17 | 29 | AHU-GYM- HRW Fault Sts | MCC
| UI8 |  | AHU-SF-01-GYM | Total Recovery Wheel Auto Status | BI-18 | 30 | AHU-GYM- HRW Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | AHU-SF-02-SWP | Supply Fan ON/OFF Status | BI-59 | 31 | AHU-SWP- SF ON/OFF Sts | MCC
| UI2 |  | AHU-SF-02-SWP | Supply Fan Trip Status | BI-60 | 32 | AHU-SWP- SF Trip Sts | MCC
| UI3 | GND | AHU-SF-02-SWP | Supply Fan Auto Position | BI-61 | 33 | AHU-SWP- SF Auto Sts | MCC
| UI4 |  | AHU-SF-02-SWP | Supply Fan Proof of Flow | BI-62 | 34 | AHU-SWP- SF Flow Sts | SWITCH
| UI5 | GND | AHU-SF-02-SWP | Exhaust Fan ON/OFF Status | BI-63 | 35 | AHU-SWP- EF ON/OFF Sts | MCC
| UI6 |  | AHU-SF-02-SWP | Exhaust Fan Trip Status | BI-64 | 36 | AHU-SWP- EF Trip Sts | MCC
| UI7 | GND | AHU-SF-02-SWP | Exhaust Fan Auto Position | BI-65 | 37 | AHU-SWP- EF Auto Sts | MCC
| UI8 |  | AHU-SF-02-SWP | Exhaust Fan Proof of Flow | BI-66 | 38 | AHU-SWP- EF Flow Sts | SWITCH
| UI9 | GND | AHU-SF-02-SWP | Fresh Air Damper Open/Close Status | BI-67 | 39 | AHU-SWP- FA Damper Sts | SWITCH
| UI10 |  | AHU-SF-02-SWP | Return Air Damper Open/Close Status | BI-68 | 40 | AHU-SWP- RA Damper Sts | SWITCH
| UI11 | GND | AHU-SF-02-SWP | Exhaust Air Damper Open/Close Status | BI-69 | 41 | AHU-SWP- EA Damper Sts | SWITCH
| UI12 |  | AHU-SF-02-SWP | Pre Filter Dirty Status | BI-70 | 42 | AHU-SWP- Pre Filter Dirty | SWITCH
| UI13 | GND | AHU-SF-02-SWP | Bag Filter Dirty Status | BI-71 | 43 | AHU-SWP- Bag Filter Dirty | SWITCH
| UI14 |  | AHU-SF-02-SWP | Total Recovery Wheel ON/OFF Status | BI-72 | 44 | AHU-SWP- HRW ON/OFF Sts | MCC
| UI15 | GND | AHU-SF-02-SWP | Total Recovery Wheel Fault Status | BI-73 | 45 | AHU-SWP- HRW Fault Sts | MCC
| UI16 |  | AHU-SF-02-SWP | Total Recovery Wheel Auto Status | BI-74 | 46 | AHU-SWP- HRW Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | SEF-RF-15 | Fan ON/OFF Status | BI-75 | 47 | SEF-RF15- ON/OFF Sts | MCC
| UI2 |  | SEF-RF-15 | Fan Trip Status | BI-76 | 48 | SEF-RF15- Trip Sts | MCC
| UI3 | GND | SEF-RF-15 | Fan Proof of Flow | BI-77 | 49 | SEF-RF15- Flow Sts | SWITCH
| UI4 |  | SEF-RF-15 | Fan in AUTO at MCC | BI-78 | 50 | SEF-RF15- Auto Sts | MCC
| UI5 | GND | SEF-RF-16 | Fan ON/OFF Status | BI-79 | 51 | SEF-RF16- ON/OFF Sts | MCC
| UI6 |  | SEF-RF-16 | Fan Trip Status | BI-80 | 52 | SEF-RF16- Trip Sts | MCC
| UI7 | GND | SEF-RF-16 | Fan Proof of Flow | BI-81 | 53 | SEF-RF16- Flow Sts | SWITCH
| UI8 |  | SEF-RF-16 | Fan in AUTO at MCC | BI-82 | 54 | SEF-RF16- Auto Sts | MCC
| UI9 | GND | PF-RF-06 | Fan Run Status | BI-83 | 55 | PF-RF06- Run Sts | MCC
| UI10 |  | PF-RF-06 | Fan Trip Status | BI-84 | 56 | PF-RF06- Trip Sts | MCC
| UI11 | GND | PF-RF-06 | Fan in OFF Position at MCC | BI-85 | 57 | PF-RF06- OFF Pos Sts | MCC
| UI12 |  | SMDB-SF-01 | Incomer Breaker Run | BI-86 | 58 | SMDB-SF01- Breaker Run | MCC
| UI13 | GND | SMDB-SF-01 | Incomer Breaker Trip | BI-87 | 59 | SMDB-SF01- Breaker Trip | MCC
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (4)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | AHU-SF-01-GYM | Supply Fan VFD Feedback | AI-91 | 60 | AHU-GYM- SF VFD Fbk | VFD
| UI2 |  | AHU-SF-01-GYM | Exhaust Fan VFD Feedback | AI-92 | 61 | AHU-GYM- EF VFD Fbk | VFD
| UI3 | GND | AHU-SF-01-GYM | CHW Valve Position Feedback | AI-93 | 62 | AHU-GYM- CHW Valve Fbk | ACTUATOR
| UI4 |  | AHU-SF-01-GYM | CHW Return Temperature | AI-94 | 63 | AHU-GYM- CHW Ret Temp | SENSOR
| UI5 | GND | AHU-SF-01-GYM | Reheat Valve Position Feedback | AI-95 | 64 | AHU-GYM- Reheat Valve Fbk | ACTUATOR
| UI6 |  | AHU-SF-02-SWP | CHW Return Temperature | AI-96 | 65 | AHU-SWP- CHW Ret Temp | SENSOR
| UI7 | GND | AHU-SF-02-SWP | Supply Fan VFD Feedback | AI-97 | 66 | AHU-SWP- SF VFD Fbk | VFD
| UI8 |  | AHU-SF-02-SWP | Exhaust Fan VFD Feedback | AI-98 | 67 | AHU-SWP- EF VFD Fbk | VFD
| UI9 | GND | AHU-SF-02-SWP | Reheat Valve Position Feedback | AI-99 | 68 | AHU-SWP- Reheat Valve Fbk | ACTUATOR
| UI10 |  | AHU-SF-02-SWP | CHW Valve Position Feedback | AI-100 | 69 | AHU-SWP- CHW Valve Fbk | ACTUATOR
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-SF-01-APS
DDC-SF-01 as per site
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | AHU-SF-01-GYM | Supply Fan-1 Start/Stop Command | BO-1 | R1 | AHU-GYM- SF Start/Stop Cmd | MCC
| UO2 |  | AHU-SF-01-GYM | Supply Fan-2 Start/Stop Command | BO-2 | R2 | AHU-GYM- EF Start/Stop Cmd | MCC
| UO3 | GND | AHU-SF-01-GYM | Exhaust Fan Start/Stop Command | BO-3 | R3 | AHU-GYM- HRW Cmd | MCC
| UO4 |  | AHU-SF-01-GYM | HRW Start/Stop Command | BO-4 | R4 | AHU-SWP- SF Start/Stop Cmd | MCC | sf-02
| UO5 | GND | AHU-SF-02-SWP | Supply Fan-1 Start/Stop Command | BO-5 | R5 | AHU-SWP- EF Start/Stop Cmd | MCC | 4 sf
| UO6 |  | AHU-SF-02-SWP | Supply Fan-2 Start/Stop Command | BO-6 | R6 | AHU-SWP- HRW Cmd | MCC | 1 ef
| UO7 | GND | AHU-SF-02-SWP | Supply Fan-3 Start/Stop Command | BO-7
| UO8 |  | AHU-SF-02-SWP | Supply Fan-4 Start/Stop Command | BO-8
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC | sf 01
|  |  | System | Point Description |  |  |  |  | 2 sf
| UI3 | GND | AHU-SF-01-GYM | Supply Fan-1 Run Status | BI-3 | 7 | AHU-GYM- SF ON/OFF Sts | MCC | 1 ef
| UI4 |  | AHU-SF-01-GYM | Supply Fan-1 Trip Status | BI-4 | 8 | AHU-GYM- SF Trip Sts | MCC
| UI5 | GND | AHU-SF-01-GYM | Supply Fan-1 Auto Position | BI-5 | 9 | AHU-GYM- SF Auto Sts | MCC
| UI6 |  | AHU-SF-01-GYM | Supply Fan-2 Run Status | BI-6 | 10 | AHU-GYM- SF Flow Sts | SWITCH
| UI7 | GND | AHU-SF-01-GYM | Supply Fan-2 Trip Status | BI-7 | 11 | AHU-GYM- EF ON/OFF Sts | MCC
| UI8 |  | AHU-SF-01-GYM | Supply Fan-2 Auto Position | BI-8 | 12 | AHU-GYM- EF Trip Sts | MCC
| UI9 | GND | AHU-SF-01-GYM | Supply Fan-Array Proof of Flow | BI-9 | 13 | AHU-GYM- EF Auto Sts | MCC
| UI10 |  | AHU-SF-01-GYM | Exhaust Fan Run Status | BI-10 | 14 | AHU-GYM- EF Flow Sts | SWITCH
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | AHU-SF-02-SWP | Exhaust Fan Start/Stop Command | BO-9
| UO2 |  | AHU-SF-02-SWP | HRW Start/Stop Command | BO-10
| UO3 | GND | AHU-SF-01-GYM | Supply Fan-1 VFD Control Signal | AO-11
| UO4 |  | AHU-SF-01-GYM | Supply Fan-2 VFD Control Signal | AO-12
| UO5 | GND | AHU-SF-01-GYM | CHW Valve Control Signal | AO-13
| UO6 |  | AHU-SF-01-GYM | Exhaust Fan VFD Control Signal | AO-14
| UO7 | GND | AHU-SF-01-GYM | Reheat Valve Control Signal | AO-15
| UO8 |  | AHU-SF-02-SWP | Supply Fan-1 VFD Control Signal | AO-16
| PIN | COM
| UI1 | GND | AHU-SF-01-GYM | Exhaust Fan Trip Status
| UI2 |  | AHU-SF-01-GYM | Exhaust Fan Auto Position
| UI3 | GND | AHU-SF-01-GYM | Exhaust Fan Proof of Flow
| UI4 |  | AHU-SF-01-GYM | Dampers Open/Close Status
| UI5 | GND | AHU-SF-01-GYM | Pre&Bag Filter Dirty Status
| UI6 |  | AHU-SF-01-GYM | Total Recovery Wheel Run Status
| UI7 | GND | AHU-SF-01-GYM | Total Recovery Wheel Trip Status
| UI8 |  | AHU-SF-01-GYM | Total Recovery Wheel Auto Status
| 24VAC | ~
0VAC
Module-FBM-8I8O (2)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | AHU-SF-02-SWP | Supply Fan-2 VFD Control Signal | AO-9 | 15 | AHU-GYM- SF VFD CMD | VFD
| UO2 |  | AHU-SF-02-SWP | Supply Fan-3 VFD Control Signal | AO-10 | 16 | AHU-GYM- CHW CMD | ACTUATOR
| UO3 | GND | AHU-SF-02-SWP | Supply Fan-4 VFD Control Signal | AO-11 | 17 | AHU-GYM- EF VFD CMD | VFD
| UO4 |  | AHU-SF-02-SWP | CHW Valve Control Signal | AO-12 | 18 | AHU-GYM- Reheat CMD | ACTUATOR
| UO5 | GND | AHU-SF-02-SWP | Exhaust Fan VFD Control Signal | AO-13 | 19 | AHU-SWP- SF VFD CMD | VFD
| UO6 |  | AHU-SF-02-SWP | Reheat Valve Control Signal | AO-14 | 20 | AHU-SWP- CHW CMD | ACTUATOR
| UO7 | GND |  |  | AO-15 | 21 | AHU-SWP- EF VFD CMD | VFD
| UO8 |  |  |  | AO-16 | 22 | AHU-SWP- Reheat CMD | ACTUATOR
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND |  | Supply Fan-1 Run Status | BI-11 | 23 | AHU-GYM- FA Damper Sts | SWITCH
| UI2 |  |  | Supply Fan-1 Trip Status | BI-12 | 24 | AHU-GYM- RA Damper Sts | SWITCH
| UI3 | GND |  | Supply Fan-1 Auto Position | BI-13 | 25 | AHU-GYM- EA Damper Sts | SWITCH
| UI4 |  |  | Supply Fan-2 Run Status | BI-14 | 26 | AHU-GYM- Pre Filter Dirty | SWITCH
| UI5 | GND |  | Supply Fan-2 Trip Status | BI-15 | 27 | AHU-GYM- Bag Filter Dirty | SWITCH
| UI6 |  |  | Supply Fan-2 Auto Position | BI-16 | 28 | AHU-GYM- HRW ON/OFF Sts | MCC
| UI7 | GND |  | Supply Fan-3 Run Status | BI-17 | 29 | AHU-GYM- HRW Fault Sts | MCC
| UI8 |  |  | Supply Fan-3 Trip Status | BI-18 | 30 | AHU-GYM- HRW Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | AHU-SF-02-SWP | Supply Fan-3 Auto Position | BI-59 | 31 | AHU-SWP- SF ON/OFF Sts | MCC
| UI2 |  | AHU-SF-02-SWP | Supply Fan-4 Run Status | BI-60 | 32 | AHU-SWP- SF Trip Sts | MCC
| UI3 | GND | AHU-SF-02-SWP | Supply Fan-4 Trip Status | BI-61 | 33 | AHU-SWP- SF Auto Sts | MCC
| UI4 |  | AHU-SF-02-SWP | Supply Fan-4 Auto Position | BI-62 | 34 | AHU-SWP- SF Flow Sts | SWITCH
| UI5 | GND | AHU-SF-02-SWP | Supply Fan-Array Proof of Flow | BI-63 | 35 | AHU-SWP- EF ON/OFF Sts | MCC
| UI6 |  | AHU-SF-02-SWP | Exhaust Fan Run Status | BI-64 | 36 | AHU-SWP- EF Trip Sts | MCC
| UI7 | GND | AHU-SF-02-SWP | Exhaust Fan Trip Status | BI-65 | 37 | AHU-SWP- EF Auto Sts | MCC
| UI8 |  | AHU-SF-02-SWP | Exhaust Fan Auto Position | BI-66 | 38 | AHU-SWP- EF Flow Sts | SWITCH
| UI9 | GND | AHU-SF-02-SWP | Exhaust Fan Proof of Flow | BI-67 | 39 | AHU-SWP- FA Damper Sts | SWITCH
| UI10 |  | AHU-SF-02-SWP | Dampers Open/Close Status | BI-68 | 40 | AHU-SWP- RA Damper Sts | SWITCH
| UI11 | GND | AHU-SF-02-SWP | Pre&Bag Filter Dirty Status | BI-69 | 41 | AHU-SWP- EA Damper Sts | SWITCH
| UI12 |  | AHU-SF-02-SWP | Total Recovery Wheel Run Status | BI-70 | 42 | AHU-SWP- Pre Filter Dirty | SWITCH
| UI13 | GND | AHU-SF-02-SWP | Total Recovery Wheel Trip Status | BI-71 | 43 | AHU-SWP- Bag Filter Dirty | SWITCH
| UI14 |  | AHU-SF-02-SWP | Total Recovery Wheel Auto Status | BI-72 | 44 | AHU-SWP- HRW ON/OFF Sts | MCC
| UI15 | GND | SEF-RF-15 | Fan Run Status | BI-73 | 45 | AHU-SWP- HRW Fault Sts | MCC
| UI16 |  | SEF-RF-15 | Fan Trip Status | BI-74 | 46 | AHU-SWP- HRW Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (4)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | SEF-RF-15 | Fan Proof of Flow | BI-75 | 47 | SEF-RF15- ON/OFF Sts | MCC
| UI2 |  | SEF-RF-15 | Fan in AUTO at MCC | BI-76 | 48 | SEF-RF15- Trip Sts | MCC
| UI3 | GND | SEF-RF-16 | Fan Run Status | BI-77 | 49 | SEF-RF15- Flow Sts | SWITCH
| UI4 |  | SEF-RF-16 | Fan Trip Status | BI-78 | 50 | SEF-RF15- Auto Sts | MCC
| UI5 | GND | SEF-RF-16 | Fan Proof of Flow | BI-79 | 51 | SEF-RF16- ON/OFF Sts | MCC
| UI6 |  | SEF-RF-16 | Fan in AUTO at MCC | BI-80 | 52 | SEF-RF16- Trip Sts | MCC
| UI7 | GND | PF-RF-06 | Fan Run Status | BI-81 | 53 | SEF-RF16- Flow Sts | SWITCH
| UI8 |  | PF-RF-06 | Fan Trip Status | BI-82 | 54 | SEF-RF16- Auto Sts | MCC
| UI9 | GND | PF-RF-06 | Fan in Auto Position at MCC | BI-83 | 55 | PF-RF06- Run Sts | MCC
| UI10 |  |  |  | BI-84 | 56 | PF-RF06- Trip Sts | MCC
| UI11 | GND |  |  | BI-85 | 57 | PF-RF06- OFF Pos Sts | MCC
| UI12 |  | SMDB-SF-01 | Incomer Breaker Run | BI-86 | 58 | SMDB-SF01- Breaker Run | MCC
| UI13 | GND | SMDB-SF-01 | Incomer Breaker Trip | BI-87 | 59 | SMDB-SF01- Breaker Trip | MCC
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (4)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | AHU-SF-01-GYM | Supply Fan VFD Feedback | AI-91 | 60 | AHU-GYM- SF VFD Fbk | VFD
| UI2 |  | AHU-SF-01-GYM | Exhaust Fan VFD Feedback | AI-92 | 61 | AHU-GYM- EF VFD Fbk | VFD
| UI3 | GND | AHU-SF-01-GYM | CHW Valve Position Feedback | AI-93 | 62 | AHU-GYM- CHW Valve Fbk | ACTUATOR
| UI4 |  | AHU-SF-01-GYM | CHW Return Temperature | AI-94 | 63 | AHU-GYM- CHW Ret Temp | SENSOR
| UI5 | GND | AHU-SF-01-GYM | Reheat Valve Position Feedback | AI-95 | 64 | AHU-GYM- Reheat Valve Fbk | ACTUATOR
| UI6 |  | AHU-SF-02-SWP | CHW Return Temperature | AI-96 | 65 | AHU-SWP- CHW Ret Temp | SENSOR
| UI7 | GND | AHU-SF-02-SWP | Supply Fan VFD Feedback | AI-97 | 66 | AHU-SWP- SF VFD Fbk | VFD
| UI8 |  | AHU-SF-02-SWP | Exhaust Fan VFD Feedback | AI-98 | 67 | AHU-SWP- EF VFD Fbk | VFD
| UI9 | GND | AHU-SF-02-SWP | Reheat Valve Position Feedback | AI-99 | 68 | AHU-SWP- Reheat Valve Fbk | ACTUATOR
| UI10 |  | AHU-SF-02-SWP | CHW Valve Position Feedback | AI-100 | 69 | AHU-SWP- CHW Valve Fbk | ACTUATOR
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-SF-02
DDC-SF-02
Project - BN-01 DDC SIZE - 800 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | HRAHU-RF-06 | Total Recovery Wheel Start/Stop Command | BO-1 | R1 | HRAHU-RF06- HRW Cmd | MCC
| UO2 |  | HRAHU-RF-06 | Supply Fan Start/Stop Command | BO-2 | R2 | HRAHU-RF06- SF Cmd | MCC
| UO3 | GND | HRAHU-RF-06 | Exhaust Fan Start/Stop Command | BO-3 | R3 | HRAHU-RF06- EF Cmd | MCC
| UO4 |  |  | SPARE
| UO5 | GND | HRAHU-RF-06 | CHW Valve Control Signal | AO-5 | 4 | HRAHU-RF06- CHW CMD | ACTUATOR
| UO6 |  | HRAHU-RF-06 | Supply Fan VFD Control Signal | AO-6 | 5 | HRAHU-RF06- SF VFD CMD | VFD
| UO7 | GND | HRAHU-RF-06 | Exhaust Fan VFD Control Signal | AO-7 | 6 | HRAHU-RF06- EF VFD CMD | VFD
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | HRAHU-RF-06 | Total Recovery Wheel ON/OFF Status | BI-3 | 7 | HRAHU-RF06- HRW ON/OFF Sts | MCC
| UI4 |  | HRAHU-RF-06 | Total Recovery Wheel Fault Status | BI-4 | 8 | HRAHU-RF06- HRW Fault Sts | MCC
| UI5 | GND | HRAHU-RF-06 | Total Recovery Wheel Auto Status | BI-5 | 9 | HRAHU-RF06- HRW Auto Sts | MCC
| UI6 |  | HRAHU-RF-06 | Fresh Air Damper Open/Close Status | BI-6 | 10 | HRAHU-RF06- FA Damper Sts | SWITCH
| UI7 | GND | HRAHU-RF-06 | Exhaust Air Damper Open/Close Status | BI-7 | 11 | HRAHU-RF06- EA Damper Sts | SWITCH
| UI8 |  | HRAHU-RF-06 | Pre-Filter Dirty Status | BI-8 | 12 | HRAHU-RF06- Pre Filter Dirty | SWITCH
| UI9 | GND | HRAHU-RF-06 | Bag Filter Dirty Status | BI-9 | 13 | HRAHU-RF06- Bag Filter Dirty | SWITCH
| UI10 |  | HRAHU-RF-06 | Supply Fan Running Status | BI-10 | 14 | HRAHU-RF06- SF Run Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | HRAHU-RF-06 | Supply Fan Trip Status | BI-43 | 15 | HRAHU-RF06- SF Trip Sts | MCC
| UI2 |  | HRAHU-RF-06 | Supply Fan Auto Status | BI-44 | 16 | HRAHU-RF06- SF Auto Sts | MCC
| UI3 | GND | HRAHU-RF-06 | Exhaust Fan Running Status | BI-45 | 17 | HRAHU-RF06- EF Run Sts | MCC
| UI4 |  | HRAHU-RF-06 | Exhaust Fan Trip Status | BI-46 | 18 | HRAHU-RF06- EF Trip Sts | MCC
| UI5 | GND | HRAHU-RF-06 | Exhaust Fan Auto Status | BI-47 | 19 | HRAHU-RF06- EF Auto Sts | MCC
| UI6 |  | HRAHU-RF-06 | Exhaust Fan Proof of Flow | BI-48 | 20 | HRAHU-RF06- EF Flow Sts | SWITCH
| UI7 | GND | SEF-RF-02 | Fan ON/OFF Status | BI-49 | 21 | SEF-RF02- ON/OFF Sts | MCC
| UI8 |  | SEF-RF-02 | Fan Trip Status | BI-50 | 22 | SEF-RF02- Trip Sts | MCC
| UI9 | GND | SEF-RF-02 | Fan Proof of Flow | BI-51 | 23 | SEF-RF02- Flow Sts | SWITCH
| UI10 |  | SEF-RF-02 | Fan in AUTO at MCC | BI-52 | 24 | SEF-RF02- Auto Sts | MCC
| UI11 | GND | PF-RF-05 | Fan Run Status | BI-53 | 25 | PF-RF05- Run Sts | MCC
| UI12 |  | PF-RF-05 | Fan Trip Status | BI-54 | 26 | PF-RF05- Trip Sts | MCC
| UI13 | GND | PF-RF-05 | Fan in OFF Position at MCC | BI-55 | 27 | PF-RF05- OFF Pos Sts | MCC
| UI14 |  | SMDB-SF1 | Incomer Breaker Run | BI-56 | 28 | SMDB-SF1- Breaker Run | MCC
| UI15 | GND | SMDB-SF1 | Incomer Breaker Trip | BI-57 | 29 | SMDB-SF1- Breaker Trip | MCC
| UI16 |  | LIFT-5 | Run Status | BI-58 | 30 | LIFT-5- Run Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | LIFT-5 | Cabin Call Alarm | BI-59 | 31 | LIFT-5- Cabin Call Alarm | MCC
| UI2 |  | LIFT-5 | Fault Status | BI-60 | 32 | LIFT-5- Fault Sts | MCC
| UI3 | GND | HRAHU-RF-06 | CHW Valve Position Feedback | BI-61 | 33 | HRAHU-RF06- CHW Valve Fbk | ACTUATOR
| UI4 |  | HRAHU-RF-06 | CHW Return Temperature | BI-62 | 34 | HRAHU-RF06- CHW Ret Temp | SENSOR
| UI5 | GND | HRAHU-RF-06 | Supply Fan VFD Feedback | BI-63 | 35 | HRAHU-RF06- SF VFD Fbk | VFD
| UI6 |  | HRAHU-RF-06 | Exhaust Fan VFD Feedback | BI-64 | 36 | HRAHU-RF06- EF VFD Fbk | VFD
| UI7 | GND | HRAHU-RF-06 | Duct Return Temperature | BI-65 | 37 | HRAHU-RF06- Duct Ret Temp | SENSOR
| UI8 |  |  | SPARE
| UI9 | GND |  | SPARE
| UI10 |  |  | SPARE
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-RF-01
DDC-RF-01
Project - BN-01 DDC SIZE - 1000 * 1000 DDC IP - BACNET ID - TBD (Ctrl-1) / TBD (Ctrl-2)
Controller 1 — DDC-ME521P ¦ BACnet ID: TBD
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | HRAHU-RF-05 | Total Recovery Wheel Start/Stop Cmd | BO-1 | R1 | HRAHU-RF05- HRW Cmd | MCC
| UO2 |  | HRAHU-RF-05 | Supply Fan Start/Stop Command | BO-2 | R2 | HRAHU-RF05- SF Cmd | MCC
| UO3 | GND | HRAHU-RF-05 | Exhaust Fan Start/Stop Command | BO-3 | R3 | HRAHU-RF05- EF Cmd | MCC
| UO4 |  | HRAHU-RF-01 | Total Recovery Wheel Start/Stop Cmd | BO-4 | R4 | HRAHU-RF01- HRW Cmd | MCC
| UO5 | GND | HRAHU-RF-01 | Supply Fan Start/Stop Command | BO-5 | R5 | HRAHU-RF01- SF Cmd | MCC
| UO6 |  | HRAHU-RF-01 | Exhaust Fan Start/Stop Command | BO-6 | R6 | HRAHU-RF01- EF Cmd | MCC
| UO7 | GND | HRAHU-RF-02 | Total Recovery Wheel Start/Stop Cmd | BO-7 | R7 | HRAHU-RF02- HRW Cmd | MCC
| UO8 |  | HRAHU-RF-02 | Supply Fan Start/Stop Command | BO-8 | R8 | HRAHU-RF02- SF Cmd | MCC
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | HRAHU-RF-05 | Total Recovery Wheel ON/OFF Status | BI-3 | 13 | HRAHU-RF05- HRW ON/OFF Sts | MCC
| UI4 |  | HRAHU-RF-05 | Total Recovery Wheel Fault Status | BI-4 | 14 | HRAHU-RF05- HRW Fault Sts | MCC
| UI5 | GND | HRAHU-RF-05 | Total Recovery Wheel Auto Status | BI-5 | 15 | HRAHU-RF05- HRW Auto Sts | MCC
| UI6 |  | HRAHU-RF-05 | Fresh Air Damper Open/Close Status | BI-5 | 15 | HRAHU-RF05- FA Damper Sts | SWITCH
| UI7 | GND | HRAHU-RF-05 | Exhaust Air Damper Open/Close Status | BI-6 | 16 | HRAHU-RF05- EA Damper Sts | SWITCH
| UI8 |  | HRAHU-RF-05 | Pre-Filter Dirty Status | BI-7 | 17 | HRAHU-RF05- Pre Filter Dirty | SWITCH
| UI9 | GND | HRAHU-RF-05 | Return Filter Dirty Status | BI-8 | 18 | HRAHU-RF05- Ret Filter Dirty | SWITCH
| UI10 |  | HRAHU-RF-05 | Supply Fan Running Status | BI-9 | 19 | HRAHU-RF05- SF Run Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | HRAHU-RF-02 | Exhaust Fan Start/Stop Command | BO-9 | R9 | HRAHU-RF02- EF Cmd | MCC
| UO2 |  | EF-RF-08 | Fan Start/Stop Command | BO-10 | R10 | EF-RF08- Start/Stop Cmd | MCC
| UO3 | GND | EF-RF-09 | Fan Start/Stop Command | BO-11 | R11 | EF-RF09- Start/Stop Cmd | MCC
| UO4 |  | EF-LG-01 | Fan Start/Stop Command | BO-12 | R12 | EF-LG01- Start/Stop Cmd | MCC
| UO5 | GND | HRAHU-RF-05 | CHW Valve Control Signal | AO-13 | 20 | HRAHU-RF05- CHW CMD | ACTUATOR
| UO6 |  | HRAHU-RF-05 | Supply Fan VFD Control Signal | AO-14 | 21 | HRAHU-RF05- SF VFD CMD | VFD
| UO7 | GND | HRAHU-RF-05 | Exhaust Fan VFD Control Signal | AO-15 | 22 | HRAHU-RF05- EF VFD CMD | VFD
| UO8 |  | HRAHU-RF-01 | CHW Valve Control Signal | AO-16 | 23 | HRAHU-RF01- CHW CMD | ACTUATOR
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | HRAHU-RF-05 | Supply Fan Trip Status | BI-10 | 24 | HRAHU-RF05- SF Trip Sts | MCC
| UI2 |  | HRAHU-RF-05 | Supply Fan Auto Status | BI-11 | 25 | HRAHU-RF05- SF Auto Sts | MCC
| UI3 | GND | HRAHU-RF-05 | Exhaust Fan Running Status | BI-12 | 26 | HRAHU-RF05- EF Run Sts | MCC
| UI4 |  | HRAHU-RF-05 | Exhaust Fan Trip Status | BI-13 | 27 | HRAHU-RF05- EF Trip Sts | MCC
| UI5 | GND | HRAHU-RF-05 | Exhaust Fan Auto Status | BI-14 | 28 | HRAHU-RF05- EF Auto Sts | MCC
| UI6 |  | HRAHU-RF-01 | Total Recovery Wheel ON/OFF Status | BI-15 | 29 | HRAHU-RF01- HRW ON/OFF Sts | MCC
| UI7 | GND | HRAHU-RF-01 | Total Recovery Wheel Fault Status | BI-16 | 30 | HRAHU-RF01- HRW Fault Sts | MCC
| UI8 |  | HRAHU-RF-01 | Total Recovery Wheel Auto Status | BI-17 | 31 | HRAHU-RF01- HRW Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-8I8O (2)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | HRAHU-RF-01 | Supply Fan VFD Control Signal | AO-17 | 32 | HRAHU-RF01- SF VFD CMD | VFD
| UO2 |  | HRAHU-RF-01 | Exhaust Fan VFD Control Signal | AO-18 | 33 | HRAHU-RF01- EF VFD CMD | VFD
| UO3 | GND | HRAHU-RF-02 | Supply Fan VFD Control Signal | AO-19 | 34 | HRAHU-RF02- SF VFD CMD | VFD
| UO4 |  | HRAHU-RF-02 | Exhaust Fan VFD Control Signal | AO-20 | 35 | HRAHU-RF02- EF VFD CMD | VFD
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | HRAHU-RF-01 | Fresh Air Damper Open/Close Status | BI-18 | 36 | HRAHU-RF01- FA Damper Sts | SWITCH
| UI2 |  | HRAHU-RF-01 | Exhaust Air Damper Open/Close Status | BI-19 | 37 | HRAHU-RF01- EA Damper Sts | SWITCH
| UI3 | GND | HRAHU-RF-01 | Pre-Filter Dirty Status | BI-20 | 38 | HRAHU-RF01- Pre Filter Dirty | SWITCH
| UI4 |  | HRAHU-RF-01 | Return Filter Dirty Status | BI-21 | 39 | HRAHU-RF01- Ret Filter Dirty | SWITCH
| UI5 | GND | HRAHU-RF-01 | Supply Fan Running Status | BI-22 | 40 | HRAHU-RF01- SF Run Sts | MCC
| UI6 |  | HRAHU-RF-01 | Supply Fan Trip Status | BI-23 | 41 | HRAHU-RF01- SF Trip Sts | MCC
| UI7 | GND | HRAHU-RF-01 | Supply Fan Auto Status | BI-24 | 42 | HRAHU-RF01- SF Auto Sts | MCC
| UI8 |  | HRAHU-RF-01 | Exhaust Fan Running Status | BI-25 | 43 | HRAHU-RF01- EF Run Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | HRAHU-RF-01 | Exhaust Fan Trip Status | BI-75 | 44 | HRAHU-RF01- EF Trip Sts | MCC
| UI2 |  | HRAHU-RF-01 | Exhaust Fan Auto Status | BI-76 | 45 | HRAHU-RF01- EF Auto Sts | MCC
| UI3 | GND | HRAHU-RF-02 | Total Recovery Wheel ON/OFF Status | BI-77 | 46 | HRAHU-RF02- HRW ON/OFF Sts | MCC
| UI4 |  | HRAHU-RF-02 | Total Recovery Wheel Fault Status | BI-78 | 47 | HRAHU-RF02- HRW Fault Sts | MCC
| UI5 | GND | HRAHU-RF-02 | Total Recovery Wheel Auto Status | BI-79 | 48 | HRAHU-RF02- HRW Auto Sts | MCC
| UI6 |  | HRAHU-RF-02 | Fresh Air Damper Open/Close Status | BI-80 | 49 | HRAHU-RF02- FA Damper Sts | SWITCH
| UI7 | GND | HRAHU-RF-02 | Exhaust Air Damper Open/Close Status | BI-81 | 50 | HRAHU-RF02- EA Damper Sts | SWITCH
| UI8 |  | HRAHU-RF-02 | Supply Fan Running Status | BI-82 | 51 | HRAHU-RF02- SF Run Sts | MCC
| UI9 | GND | HRAHU-RF-02 | Supply Fan Trip Status | BI-83 | 52 | HRAHU-RF02- SF Trip Sts | MCC
| UI10 |  | HRAHU-RF-02 | Supply Fan Auto Status | BI-84 | 53 | HRAHU-RF02- SF Auto Sts | MCC
| UI11 | GND | HRAHU-RF-02 | Exhaust Fan Running Status | BI-85 | 54 | HRAHU-RF02- EF Run Sts | MCC
| UI12 |  | HRAHU-RF-02 | Exhaust Fan Trip Status | BI-86 | 55 | HRAHU-RF02- EF Trip Sts | MCC
| UI13 | GND | HRAHU-RF-02 | Exhaust Fan Auto Status | BI-87 | 56 | HRAHU-RF02- EF Auto Sts | MCC
| UI14 |  | EF-RF-08 | Fan Running Status | BI-88 | 57 | EF-RF08- Run Sts | MCC
| UI15 | GND | EF-RF-08 | Fan Trip Status | BI-89 | 58 | EF-RF08- Trip Sts | MCC
| UI16 |  | EF-RF-08 | Fan Auto Status | BI-90 | 59 | EF-RF08- Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (4)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | EF-RF-09 | Fan Running Status | BI-91 | 60 | EF-RF09- Run Sts | MCC
| UI2 |  | EF-RF-09 | Fan Trip Status | BI-92 | 61 | EF-RF09- Trip Sts | MCC
| UI3 | GND | EF-RF-09 | Fan Auto Status | BI-93 | 62 | EF-RF09- Auto Sts | MCC
| UI4 |  | EF-LG-01 | Fan Running Status | BI-94 | 63 | EF-LG01- Run Sts | MCC
| UI5 | GND | EF-LG-01 | Fan Trip Status | BI-95 | 64 | EF-LG01- Trip Sts | MCC
| UI6 |  | EF-LG-01 | Fan Auto Status | BI-96 | 65 | EF-LG01- Auto Sts | MCC
| UI7 | GND | HP-BNSP2-RF-01 | Duty Pump Run Status | BI-97 | 66 | HP-RF01- Duty Pump Run Sts | MCC
| UI8 |  | HP-BNSP2-RF-01 | Duty Pump Trip Status | BI-98 | 67 | HP-RF01- Duty Pump Trip Sts | MCC
| UI9 | GND | HP-BNSP2-RF-01 | Standby Pump Run Status | BI-99 | 68 | HP-RF01- Stby Pump Run Sts | MCC
| UI10 |  | HP-BNSP2-RF-01 | Standby Pump Trip Status | BI-100 | 69 | HP-RF01- Stby Pump Trip Sts | MCC
| UI11 | GND | HP-BNSP2-RF-02 | Duty Pump Run Status | BI-101 | 70 | HP-RF02- Duty Pump Run Sts | MCC
| UI12 |  | HP-BNSP2-RF-02 | Duty Pump Trip Status | BI-102 | 71 | HP-RF02- Duty Pump Trip Sts | MCC
| UI13 | GND | HP-BNSP2-RF-02 | Standby Pump Run Status | BI-103 | 72 | HP-RF02- Stby Pump Run Sts | MCC
| UI14 |  | HP-BNSP2-RF-02 | Standby Pump Trip Status | BI-104 | 73 | HP-RF02- Stby Pump Trip Sts | MCC
| UI15 | GND | PRESS.UNIT-RF-01 | Duty Pump Run Status | BI-105 | 74 | Press-RF01- Duty Pump Run Sts | MCC
| UI16 |  | PRESS.UNIT-RF-01 | Duty Pump Trip Status | BI-106 | 75 | Press-RF01- Duty Pump Trip Sts | MCC
| 24VAC | ~
0VAC
Controller 2 — DDC-ME521P ¦ BACnet ID: TBD
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND |  | SPARE
| UO2 |  |  | SPARE
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | PRESS.UNIT-RF-01 | Standby Pump Run Status | BI-3 | 76 | Press-RF01- Stby Pump Run Sts | MCC
| UI4 |  | PRESS.UNIT-RF-01 | Standby Pump Trip Status | BI-4 | 77 | Press-RF01- Stby Pump Trip Sts | MCC
| UI5 | GND | SMDB-RF-01 | Incomer Breaker Run | BI-5 | 78 | SMDB-RF01- Breaker Run | MCC
| UI6 |  | SMDB-RF-01 | Incomer Breaker Trip | BI-6 | 79 | SMDB-RF01- Breaker Trip | MCC
| UI7 | GND | ESMDB-RF-01 | Incomer Breaker Run | BI-7 | 80 | ESMDB-RF01- Breaker Run | MCC
| UI8 |  | ESMDB-RF-01 | Incomer Breaker Trip | BI-8 | 81 | ESMDB-RF01- Breaker Trip | MCC
| UI9 | GND |  | SPARE
| UI10 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | HRAHU-RF-05 | CHW Valve Position Feedback | AI-43 | 82 | HRAHU-RF05- CHW Valve Fbk | ACTUATOR
| UI2 |  | HRAHU-RF-05 | CHW Return Temperature | AI-44 | 83 | HRAHU-RF05- CHW Ret Temp | SENSOR
| UI3 | GND | HRAHU-RF-01 | CHW Valve Position Feedback | AI-45 | 84 | HRAHU-RF01- CHW Valve Fbk | ACTUATOR
| UI4 |  | HRAHU-RF-01 | CHW Return Temperature | AI-46 | 85 | HRAHU-RF01- CHW Ret Temp | SENSOR
| UI5 | GND | PRESS.UNIT-RF-01 | Line Pressure | AI-47 | 86 | Press-RF01- Line Pressure | SENSOR
| UI6 |  | HRAHU-RF-05 | Duct Return Temperature | AI-48 | 87 | HRAHU-RF05- Duct Ret Temp | SENSOR
| UI7 | GND | HRAHU-RF-01 | Duct Return Temperature | AI-49 | 88 | HRAHU-RF01- Duct Ret Temp | SENSOR
| UI8 |  | HRAHU-RF-01 | Supply Fan VFD Feedback | AI-50 | 89 | HRAHU-RF01- SF VFD Fbk | VFD
| UI9 | GND | HRAHU-RF-01 | Exhaust Fan VFD Feedback | AI-51 | 90 | HRAHU-RF01- EF VFD Fbk | VFD
| UI10 |  | HRAHU-RF-05 | Supply Fan VFD Feedback | AI-52 | 91 | HRAHU-RF05- SF VFD Fbk | VFD
| UI11 | GND | HRAHU-RF-05 | Exhaust Fan VFD Feedback | AI-53 | 92 | HRAHU-RF05- EF VFD Fbk | VFD
| UI12 |  | HRAHU-RF-02 | Supply Fan VFD Feedback | AI-54 | 93 | HRAHU-RF02- SF VFD Fbk | VFD
| UI13 | GND | HRAHU-RF-02 | Exhaust Fan VFD Feedback | AI-55 | 94 | HRAHU-RF02- EF VFD Fbk | VFD
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-RF-02
DDC-RF-02
Project - BN-01 DDC SIZE - 800 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | EF-RF-01 | Fan Start/Stop Command | BO-1 | R1 | EF-RF01- Start/Stop Cmd | MCC
| UO2 |  | EF-RF-02 | Fan Start/Stop Command | BO-2 | R2 | EF-RF02- Start/Stop Cmd | MCC
| UO3 |  |  | SPARE
| UO4 |  | BOOST.PUMP-RF-01 | Duty Pump 1 Enable/Disable Command | BO-4 | R4 | BP-RF01- Duty 1 Cmd | MCC
| UO5 | GND | BOOST.PUMP-RF-01 | Duty Pump 2 Enable/Disable Command | BO-5 | R5 | BP-RF01- Duty 2 Cmd | MCC
| UO6 |  | BOOST.PUMP-RF-01 | Standby Pump Enable/Disable Command | BO-6 | R6 | BP-RF01- Standby Cmd | MCC
| UO7 | GND | HW.CIRC.PUMP-RF-01 | Duty Pump Start/Stop Command | BO-7 | R7 | HW-Circ-RF01- Duty Cmd | MCC
| UO8 |  | HW.CIRC.PUMP-RF-01 | Standby Pump Start/Stop Command | BO-8 | R8 | HW-Circ-RF01- Standby Cmd | MCC
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | SEF-RF-06 | Fan ON/OFF Status | BI-3 | 9 | SEF-RF06- ON/OFF Sts | MCC
| UI4 |  | SEF-RF-06 | Fan Trip Status | BI-4 | 10 | SEF-RF06- Trip Sts | MCC
| UI5 | GND | SEF-RF-06 | Fan Proof of Flow | BI-5 | 11 | SEF-RF06- Flow Sts | SWITCH
| UI6 |  | SEF-RF-06 | Fan in AUTO at MCC | BI-6 | 12 | SEF-RF06- Auto Sts | MCC
| UI7 | GND | EF-RF-01 | Fan Running Status | BI-7 | 13 | EF-RF01- Run Sts | MCC
| UI8 |  | EF-RF-01 | Fan Trip Status | BI-8 | 14 | EF-RF01- Trip Sts | MCC
| UI9 | GND | EF-RF-01 | Fan Auto Status | BI-9 | 15 | EF-RF01- Auto Sts | MCC
| UI10 |  | EF-RF-02 | Fan Running Status | BI-10 | 16 | EF-RF02- Run Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | CW.CIRC.PUMP-RF-01 | Duty Pump Start/Stop Command | BO-9 | R9 | CW-Circ-RF01- Duty Cmd | MCC
| UO2 |  | CW.CIRC.PUMP-RF-01 | Standby Pump Start/Stop Command | BO-10 | R10 | CW-Circ-RF01- Standby Cmd | MCC
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | EF-RF-02 | Fan Trip Status | BI-11 | 17 | EF-RF02- Trip Sts | MCC
| UI2 |  | EF-RF-02 | Fan Auto Status | BI-12 | 18 | EF-RF02- Auto Sts | MCC
| UI3 |  | MAF-RF-06 | Fan ON/OFF Status | BI-16 | 22 | MAF-RF06- ON/OFF Sts | MCC
| UI4 |  | MAF-RF-06 | Fan Trip Status | BI-17 | 23 | MAF-RF06- Trip Sts | MCC
| UI5 |  | MAF-RF-06 | Fan Proof of Flow | BI-18 | 24 | MAF-RF06- Flow Sts | SWITCH
| UI6 |  | MAF-RF-06 | Fan in AUTO at MCC | BI-19 | 25 | MAF-RF06- Auto Sts | MCC
| UI7 | GND | PF-RF-02 | Fan Run Status | BI-20 | 26 | PF-RF02- Run Sts | MCC
| UI8 |  | PF-RF-02 | Fan Trip Status | BI-21 | 27 | PF-RF02- Trip Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | PF-RF-02 | Fan in OFF Position at MCC | BI-59 | 25 | PF-RF02- OFF Pos Sts | MCC
| UI2 |  | BOOST.PUMP-RF-01 | Duty Pump 1 Run Status | BI-60 | 26 | BP-RF01- Duty 1 Run Sts | MCC
| UI3 | GND | BOOST.PUMP-RF-01 | Duty Pump 1 Trip Status | BI-61 | 27 | BP-RF01- Duty 1 Trip Sts | MCC
| UI4 |  | BOOST.PUMP-RF-01 | Duty Pump 1 Auto Status | BI-62 | 28 | BP-RF01- Duty 1 Auto Sts | MCC
| UI5 | GND | BOOST.PUMP-RF-01 | Duty Pump 2 Run Status | BI-63 | 29 | BP-RF01- Duty 2 Run Sts | MCC
| UI6 |  | BOOST.PUMP-RF-01 | Duty Pump 2 Trip Status | BI-64 | 30 | BP-RF01- Duty 2 Trip Sts | MCC
| UI7 | GND | BOOST.PUMP-RF-01 | Duty Pump 2 Auto Status | BI-65 | 31 | BP-RF01- Duty 2 Auto Sts | MCC
| UI8 |  | BOOST.PUMP-RF-01 | Standby Pump Run Status | BI-66 | 32 | BP-RF01- Standby Run Sts | MCC
| UI9 | GND | BOOST.PUMP-RF-01 | Standby Pump Trip Status | BI-67 | 33 | BP-RF01- Standby Trip Sts | MCC
| UI10 |  | BOOST.PUMP-RF-01 | Standby Pump Auto Status | BI-68 | 34 | BP-RF01- Standby Auto Sts | MCC
| UI11 | GND | HW.CIRC.PUMP-RF-01 | Duty Pump Run Status | BI-69 | 35 | HW-Circ-RF01- Duty Run Sts | MCC
| UI12 |  | HW.CIRC.PUMP-RF-01 | Duty Pump Trip Status | BI-70 | 36 | HW-Circ-RF01- Duty Trip Sts | MCC
| UI13 | GND | HW.CIRC.PUMP-RF-01 | Duty Pump Auto Status | BI-71 | 37 | HW-Circ-RF01- Duty Auto Sts | MCC
| UI14 |  | HW.CIRC.PUMP-RF-01 | Standby Pump Run Status | BI-72 | 38 | HW-Circ-RF01- Stby Run Sts | MCC
| UI15 | GND | HW.CIRC.PUMP-RF-01 | Standby Pump Trip Status | BI-73 | 39 | HW-Circ-RF01- Stby Trip Sts | MCC
| UI16 |  | HW.CIRC.PUMP-RF-01 | Standby Pump Auto Status | BI-74 | 40 | HW-Circ-RF01- Stby Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | CW.CIRC.PUMP-RF-01 | Duty Pump Run Status | BI-75 | 41 | CW-Circ-RF01- Duty Run Sts | MCC
| UI2 |  | CW.CIRC.PUMP-RF-01 | Duty Pump Trip Status | BI-76 | 42 | CW-Circ-RF01- Duty Trip Sts | MCC
| UI3 | GND | CW.CIRC.PUMP-RF-01 | Duty Pump Auto Status | BI-77 | 43 | CW-Circ-RF01- Duty Auto Sts | MCC
| UI4 |  | CW.CIRC.PUMP-RF-01 | Standby Pump Run Status | BI-78 | 44 | CW-Circ-RF01- Stby Run Sts | MCC
| UI5 | GND | CW.CIRC.PUMP-RF-01 | Standby Pump Trip Status | BI-79 | 45 | CW-Circ-RF01- Stby Trip Sts | MCC
| UI6 |  | CW.CIRC.PUMP-RF-01 | Standby Pump Auto Status | BI-80 | 46 | CW-Circ-RF01- Stby Auto Sts | MCC
| UI7 | GND | CU/AG.IONIZER-RF-01 | Unit ON/OFF Status | BI-81 | 47 | Cu-Ag-Ionizer- ON/OFF Sts | MCC
| UI8 |  | CU/AG.IONIZER-RF-01 | Common Fault Alarm | BI-82 | 48 | Cu-Ag-Ionizer- Fault Sts | MCC
| UI9 | GND | UV.STERILIZATION-RF-01 | Filter Dirty Status | BI-83 | 49 | UV-Steril-RF01- Filter Dirty | SWITCH
| UI10 |  | CHEM.DOSING-RF-01 | Unit ON/OFF Status | BI-84 | 50 | Chem-Dosing-RF01- ON/OFF Sts | MCC
| UI11 | GND | CHEM.DOSING-RF-01 | Common Fault Alarm | BI-85 | 51 | Chem-Dosing-RF01- Fault Sts | MCC
| UI12 |  |  | SPARE
| UI13 | GND | WATER.TANK-RF-01 | Tank Level | AI-87 | 53 | Water-Tank-RF01- Level | SENSOR
| UI14 |  | WATER.TANK-RF-02 | Tank Level | AI-88 | 54 | Water-Tank-RF02- Level | SENSOR
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-RF-03
DDC-RF-03
Project - BN-01 DDC SIZE - 800 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | AHU-RF-01-DX | Supply Fan Start/Stop Command | BO-1 | R1 | AHU-RF01-DX- SF Cmd | MCC
| UO2 |  | AHU-RF-01-DX | CU Start/Stop Command | BO-2 | R2 | AHU-RF01-DX- CU Cmd | MCC
| UO3 | GND | EF-RF-03 | Fan Start/Stop Command | BO-3 | R3 | EF-RF03- Start/Stop Cmd | MCC
| UO4 |  | EF-RF-11 | Fan Start/Stop Command | BO-4 | R4 | EF-RF11- Start/Stop Cmd | MCC
| UO5 | GND | HRAHU-RF-02 | CHW Valve Control Signal | AO-5 | 5 | HRAHU-RF02- CHW CMD | ACTUATOR
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | HRAHU-RF-02 | Pre-Filter Dirty Status | BI-3 | 6 | HRAHU-RF02- Pre Filter Dirty | SWITCH
| UI4 |  | HRAHU-RF-02 | Return Filter Dirty Status | BI-4 | 7 | HRAHU-RF02- Ret Filter Dirty | SWITCH
| UI5 | GND | HRAHU-RF-02 | Supply Fan Proof of Flow | BI-5 | 8 | HRAHU-RF02- SF Flow Sts | SWITCH
| UI6 |  | HRAHU-RF-02 | Exhaust Fan Proof of Flow | BI-6 | 9 | HRAHU-RF02- EF Flow Sts | SWITCH
| UI7 | GND | AHU-RF-01-DX | Fresh Air Damper Open/Close Status | BI-7 | 10 | AHU-RF01-DX- FA Damper Sts | SWITCH
| UI8 |  | AHU-RF-01-DX | Return Air Damper Open/Close Status | BI-8 | 11 | AHU-RF01-DX- RA Damper Sts | SWITCH
| UI9 | GND | AHU-RF-01-DX | Pre-Filter Dirty Status | BI-9 | 12 | AHU-RF01-DX- Pre Filter Dirty | SWITCH
| UI10 |  | AHU-RF-01-DX | Bag Filter Dirty Status | BI-10 | 13 | AHU-RF01-DX- Bag Filter Dirty | SWITCH
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | AHU-RF-01-DX | Supply Fan Run Status | BI-43 | 14 | AHU-RF01-DX- SF Run Sts | MCC
| UI2 |  | AHU-RF-01-DX | Supply Fan Trip Status | BI-44 | 15 | AHU-RF01-DX- SF Trip Sts | MCC
| UI3 | GND | AHU-RF-01-DX | Supply Fan HOA Status | BI-45 | 16 | AHU-RF01-DX- SF HOA Sts | MCC
| UI4 |  | AHU-RF-01-DX | CU Run Status | BI-46 | 17 | AHU-RF01-DX- CU Run Sts | MCC
| UI5 | GND | EF-RF-03 | Fan Running Status | BI-47 | 18 | EF-RF03- Run Sts | MCC
| UI6 |  | EF-RF-03 | Fan Trip Status | BI-48 | 19 | EF-RF03- Trip Sts | MCC
| UI7 | GND | EF-RF-03 | Fan Auto Status | BI-49 | 20 | EF-RF03- Auto Sts | MCC
| UI8 |  | EF-RF-11 | Fan Running Status | BI-50 | 21 | EF-RF11- Run Sts | MCC
| UI9 | GND | EF-RF-11 | Fan Trip Status | BI-51 | 22 | EF-RF11- Trip Sts | MCC
| UI10 |  | EF-RF-11 | Fan Auto Status | BI-52 | 23 | EF-RF11- Auto Sts | MCC
| UI11 | GND | SEF-RF-01 | Fan ON/OFF Status | BI-53 | 24 | SEF-RF01- ON/OFF Sts | MCC
| UI12 |  | SEF-RF-01 | Fan Trip Status | BI-54 | 25 | SEF-RF01- Trip Sts | MCC
| UI13 | GND | SEF-RF-01 | Fan Proof of Flow | BI-55 | 26 | SEF-RF01- Flow Sts | SWITCH
| UI14 |  | SEF-RF-01 | Fan in AUTO at MCC | BI-56 | 27 | SEF-RF01- Auto Sts | MCC
| UI15 | GND | SEF-RF-04 | Fan ON/OFF Status | BI-57 | 28 | SEF-RF04- ON/OFF Sts | MCC
| UI16 |  | SEF-RF-04 | Fan Trip Status | BI-58 | 29 | SEF-RF04- Trip Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | SEF-RF-04 | Fan Proof of Flow | BI-59 | 30 | SEF-RF04- Flow Sts | SWITCH
| UI2 |  | SEF-RF-04 | Fan in AUTO at MCC | BI-60 | 31 | SEF-RF04- Auto Sts | MCC
| UI3 | GND | MAF-RF-01 | Fan ON/OFF Status | BI-61 | 32 | MAF-RF01- ON/OFF Sts | MCC
| UI4 |  | MAF-RF-01 | Fan Trip Status | BI-62 | 33 | MAF-RF01- Trip Sts | MCC
| UI5 | GND | MAF-RF-01 | Fan Proof of Flow | BI-63 | 34 | MAF-RF01- Flow Sts | SWITCH
| UI6 |  | MAF-RF-01 | Fan in AUTO at MCC | BI-64 | 35 | MAF-RF01- Auto Sts | MCC
| UI7 | GND | MAF-RF-04 | Fan ON/OFF Status | BI-65 | 36 | MAF-RF04- ON/OFF Sts | MCC
| UI8 |  | MAF-RF-04 | Fan Trip Status | BI-66 | 37 | MAF-RF04- Trip Sts | MCC
| UI9 | GND | MAF-RF-04 | Fan Proof of Flow | BI-67 | 38 | MAF-RF04- Flow Sts | SWITCH
| UI10 |  | MAF-RF-04 | Fan in AUTO at MCC | BI-68 | 39 | MAF-RF04- Auto Sts | MCC
| UI11 | GND | PF-RF-02 | Fan Run Status | BI-69 | 40 | PF-RF02- Run Sts | MCC
| UI12 |  | PF-RF-02 | Fan Trip Status | BI-70 | 41 | PF-RF02- Trip Sts | MCC
| UI13 | GND | PF-RF-02 | Fan in OFF Position at MCC | BI-71 | 42 | PF-RF02- OFF Pos Sts | MCC
| UI14 |  | SMDB-SF-4 | Incomer Breaker Run | BI-72 | 43 | SMDB-SF4- Breaker Run | MCC
| UI15 | GND | SMDB-SF-4 | Incomer Breaker Trip | BI-73 | 44 | SMDB-SF4- Breaker Trip | MCC
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | HRAHU-RF-02 | CHW Valve Position Feedback | AI-75 | 38 | HRAHU-RF02- CHW Valve Fbk | ACTUATOR
| UI2 |  | HRAHU-RF-02 | CHW Return Temperature | AI-76 | 39 | HRAHU-RF02- CHW Ret Temp | SENSOR
| UI3 | GND | HRAHU-RF-02 | Duct Return Temperature | AI-77 | 40 | HRAHU-RF02- Duct Ret Temp | SENSOR
| UI4 |  | AHU-RF-01-DX | Return Temperature | AI-78 | 41 | AHU-RF01-DX- Return Temp | SENSOR
| UI5 | GND |  | SPARE
| UI6 |  |  | SPARE
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| UI9 | GND |  | SPARE
| UI10 |  |  | SPARE
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-RF-04
DDC-RF-04
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | HRAHU-RF-03 | Total Recovery Wheel Start/Stop Cmd | BO-1 | R1 | HRAHU-RF03- HRW Cmd | MCC
| UO2 |  | HRAHU-RF-03 | Supply Fan Start/Stop Command | BO-2 | R2 | HRAHU-RF03- SF Cmd | MCC
| UO3 | GND | HRAHU-RF-03 | Exhaust Fan Start/Stop Command | BO-3 | R3 | HRAHU-RF03- EF Cmd | MCC
| UO4 |  | HRAHU-RF-04 | Total Recovery Wheel Start/Stop Cmd | BO-4 | R4 | HRAHU-RF04- HRW Cmd | MCC
| UO5 | GND | HRAHU-RF-04 | Supply Fan Start/Stop Command | BO-5 | R5 | HRAHU-RF04- SF Cmd | MCC
| UO6 |  | HRAHU-RF-04 | Exhaust Fan Start/Stop Command | BO-6 | R6 | HRAHU-RF04- EF Cmd | MCC
| UO7 | GND | HRAHU-RF-03 | Supply Fan VFD Control Signal | AO-7 | 7 | HRAHU-RF03- SF VFD CMD | VFD
| UO8 |  | HRAHU-RF-03 | Exhaust Fan VFD Control Signal | AO-8 | 8 | HRAHU-RF03- EF VFD CMD | VFD
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | HRAHU-RF-03 | Total Recovery Wheel ON/OFF Status | BI-3 | 9 | HRAHU-RF03- HRW ON/OFF Sts | MCC
| UI4 |  | HRAHU-RF-03 | Total Recovery Wheel Fault Status | BI-4 | 10 | HRAHU-RF03- HRW Fault Sts | MCC
| UI5 | GND | HRAHU-RF-03 | Total Recovery Wheel Auto Status | BI-5 | 11 | HRAHU-RF03- HRW Auto Sts | MCC
| UI6 |  | HRAHU-RF-03 | Fresh Air Damper Open/Close Status | BI-6 | 12 | HRAHU-RF03- FA Damper Sts | SWITCH
| UI7 | GND | HRAHU-RF-03 | Exhaust Air Damper Open/Close Status | BI-7 | 13 | HRAHU-RF03- EA Damper Sts | SWITCH
| UI8 |  | HRAHU-RF-03 | Supply Fan Running Status | BI-8 | 14 | HRAHU-RF03- SF Run Sts | MCC
| UI9 | GND | HRAHU-RF-03 | Supply Fan Trip Status | BI-9 | 15 | HRAHU-RF03- SF Trip Sts | MCC
| UI10 |  | HRAHU-RF-03 | Supply Fan Auto Status | BI-10 | 16 | HRAHU-RF03- SF Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | HRAHU-RF-04 | Supply Fan VFD Control Signal | AO-9 | 17 | HRAHU-RF04- SF VFD CMD | VFD
| UO2 |  | HRAHU-RF-04 | Exhaust Fan VFD Control Signal | AO-10 | 18 | HRAHU-RF04- EF VFD CMD | VFD
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | HRAHU-RF-03 | Exhaust Fan Running Status | BI-11 | 19 | HRAHU-RF03- EF Run Sts | MCC
| UI2 |  | HRAHU-RF-03 | Exhaust Fan Trip Status | BI-12 | 20 | HRAHU-RF03- EF Trip Sts | MCC
| UI3 | GND | HRAHU-RF-03 | Exhaust Fan Auto Status | BI-13 | 21 | HRAHU-RF03- EF Auto Sts | MCC
| UI4 |  | HRAHU-RF-04 | Total Recovery Wheel ON/OFF Status | BI-14 | 22 | HRAHU-RF04- HRW ON/OFF Sts | MCC
| UI5 | GND | HRAHU-RF-04 | Total Recovery Wheel Fault Status | BI-15 | 23 | HRAHU-RF04- HRW Fault Sts | MCC
| UI6 |  | HRAHU-RF-04 | Total Recovery Wheel Auto Status | BI-16 | 24 | HRAHU-RF04- HRW Auto Sts | MCC
| UI7 | GND | HRAHU-RF-04 | Fresh Air Damper Open/Close Status | BI-17 | 25 | HRAHU-RF04- FA Damper Sts | SWITCH
| UI8 |  | HRAHU-RF-04 | Exhaust Air Damper Open/Close Status | BI-18 | 26 | HRAHU-RF04- EA Damper Sts | SWITCH
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | HRAHU-RF-04 | Supply Fan Running Status | BI-59 | 27 | HRAHU-RF04- SF Run Sts | MCC
| UI2 |  | HRAHU-RF-04 | Supply Fan Trip Status | BI-60 | 28 | HRAHU-RF04- SF Trip Sts | MCC
| UI3 | GND | HRAHU-RF-04 | Supply Fan Auto Status | BI-61 | 29 | HRAHU-RF04- SF Auto Sts | MCC
| UI4 |  | HRAHU-RF-04 | Exhaust Fan Running Status | BI-62 | 30 | HRAHU-RF04- EF Run Sts | MCC
| UI5 | GND | HRAHU-RF-04 | Exhaust Fan Trip Status | BI-63 | 31 | HRAHU-RF04- EF Trip Sts | MCC
| UI6 |  | HRAHU-RF-04 | Exhaust Fan Auto Status | BI-64 | 32 | HRAHU-RF04- EF Auto Sts | MCC
| UI7 | GND | SEF-RF-03 | Fan ON/OFF Status | BI-65 | 33 | SEF-RF03- ON/OFF Sts | MCC
| UI8 |  | SEF-RF-03 | Fan Trip Status | BI-66 | 34 | SEF-RF03- Trip Sts | MCC
| UI9 | GND | SEF-RF-03 | Fan Proof of Flow | BI-67 | 35 | SEF-RF03- Flow Sts | SWITCH
| UI10 |  | SEF-RF-03 | Fan in AUTO at MCC | BI-68 | 36 | SEF-RF03- Auto Sts | MCC
| UI11 | GND | MAF-RF-03 | Fan ON/OFF Status | BI-69 | 37 | MAF-RF03- ON/OFF Sts | MCC
| UI12 |  | MAF-RF-03 | Fan Trip Status | BI-70 | 38 | MAF-RF03- Trip Sts | MCC
| UI13 | GND | MAF-RF-03 | Fan Proof of Flow | BI-71 | 39 | MAF-RF03- Flow Sts | SWITCH
| UI14 |  | MAF-RF-03 | Fan in AUTO at MCC | BI-72 | 40 | MAF-RF03- Auto Sts | MCC
| UI15 | GND | SMDB-RF2 | Incomer Breaker Run | BI-73 | 41 | SMDB-RF2- Breaker Run | MCC
| UI16 |  | SMDB-RF2 | Incomer Breaker Trip | BI-74 | 42 | SMDB-RF2- Breaker Trip | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | SMDB-SF3 | Incomer Breaker Run | BI-75 | 43 | SMDB-SF3- Breaker Run | MCC
| UI2 |  | SMDB-SF3 | Incomer Breaker Trip | BI-76 | 44 | SMDB-SF3- Breaker Trip | MCC
| UI3 | GND | ESMDB-RF2 | Incomer Breaker Run | BI-77 | 45 | ESMDB-RF2- Breaker Run | MCC
| UI4 |  | ESMDB-RF2 | Incomer Breaker Trip | BI-78 | 46 | ESMDB-RF2- Breaker Trip | MCC
| UI5 | GND | NOVEC-8 | Unit Normal/Fault Status | BI-79 | 47 | NOVEC-8- Normal/Fault | MCC
| UI6 |  |  | SPARE
| UI7 | GND | HRAHU-RF-03 | Supply Fan VFD Feedback | AI-81 | 48 | HRAHU-RF03- SF VFD Fbk | VFD
| UI8 |  | HRAHU-RF-03 | Exhaust Fan VFD Feedback | AI-82 | 49 | HRAHU-RF03- EF VFD Fbk | VFD
| UI9 | GND | HRAHU-RF-04 | Supply Fan VFD Feedback | AI-83 | 50 | HRAHU-RF04- SF VFD Fbk | VFD
| UI10 |  | HRAHU-RF-04 | Exhaust Fan VFD Feedback | AI-84 | 51 | HRAHU-RF04- EF VFD Fbk | VFD
| UI11 | GND | OUTSIDE- T/H SENSOR | Outside Temperature | AI-85 | 52 | Outside- Temperature | SENSOR
| UI12 |  | OUTSIDE- T/H SENSOR | Outside Humidity | AI-86 | 53 | Outside- Humidity | SENSOR
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-RF-05
DDC-RF-05
Project - BN-01 DDC SIZE - 800 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | EF-RF-04 | Fan Start/Stop Command | BO-1 | R1 | EF-RF04- Start/Stop Cmd | MCC
| UO2 |  | EF-RF-05 | Fan Start/Stop Command | BO-2 | R2 | EF-RF05- Start/Stop Cmd | MCC
| UO3 | GND | EF-RF-06 | Fan Start/Stop Command | BO-3 | R3 | EF-RF06- Start/Stop Cmd | MCC
| UO4 |  | EF-RF-07 | Fan Start/Stop Command | BO-4 | R4 | EF-RF07- Start/Stop Cmd | MCC
| UO5 | GND | HRAHU-RF-03 | CHW Valve Control Signal | AO-5 | 5 | HRAHU-RF03- CHW CMD | ACTUATOR
| UO6 |  | HRAHU-RF-04 | CHW Valve Control Signal | AO-6 | 6 | HRAHU-RF04- CHW CMD | ACTUATOR
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | SEF-RF-05 | Fan ON/OFF Status | BI-3 | 7 | SEF-RF05- ON/OFF Sts | MCC
| UI4 |  | SEF-RF-05 | Fan Trip Status | BI-4 | 8 | SEF-RF05- Trip Sts | MCC
| UI5 | GND | SEF-RF-05 | Fan Proof of Flow | BI-5 | 9 | SEF-RF05- Flow Sts | SWITCH
| UI6 |  | SEF-RF-05 | Fan in AUTO at MCC | BI-6 | 10 | SEF-RF05- Auto Sts | MCC
| UI7 | GND | MAF-RF-05 | Fan ON/OFF Status | BI-7 | 11 | MAF-RF05- ON/OFF Sts | MCC
| UI8 |  | MAF-RF-05 | Fan Trip Status | BI-8 | 12 | MAF-RF05- Trip Sts | MCC
| UI9 | GND | MAF-RF-05 | Fan Proof of Flow | BI-9 | 13 | MAF-RF05- Flow Sts | SWITCH
| UI10 |  | MAF-RF-05 | Fan in AUTO at MCC | BI-10 | 14 | MAF-RF05- Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND |  | SPARE
| UO2 |  |  | SPARE
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | HRAHU-RF-03 | Pre-Filter Dirty Status | BI-11 | 15 | HRAHU-RF03- Pre Filter Dirty | SWITCH
| UI2 |  | HRAHU-RF-03 | Return Filter Dirty Status | BI-12 | 16 | HRAHU-RF03- Ret Filter Dirty | SWITCH
| UI3 | GND | HRAHU-RF-03 | Supply Fan Proof of Flow | BI-13 | 17 | HRAHU-RF03- SF Flow Sts | SWITCH
| UI4 |  | HRAHU-RF-03 | Exhaust Fan Proof of Flow | BI-14 | 18 | HRAHU-RF03- EF Flow Sts | SWITCH
| UI5 | GND | HRAHU-RF-04 | Pre-Filter Dirty Status | BI-15 | 19 | HRAHU-RF04- Pre Filter Dirty | SWITCH
| UI6 |  | HRAHU-RF-04 | Return Filter Dirty Status | BI-16 | 20 | HRAHU-RF04- Ret Filter Dirty | SWITCH
| UI7 | GND | HRAHU-RF-04 | Supply Fan Proof of Flow | BI-17 | 21 | HRAHU-RF04- SF Flow Sts | SWITCH
| UI8 |  | HRAHU-RF-04 | Exhaust Fan Proof of Flow | BI-18 | 22 | HRAHU-RF04- EF Flow Sts | SWITCH
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | EF-RF-04 | Fan Running Status | BI-59 | 23 | EF-RF04- Run Sts | MCC
| UI2 |  | EF-RF-04 | Fan Trip Status | BI-60 | 24 | EF-RF04- Trip Sts | MCC
| UI3 | GND | EF-RF-04 | Fan Auto Status | BI-61 | 25 | EF-RF04- Auto Sts | MCC
| UI4 |  | EF-RF-05 | Fan Running Status | BI-62 | 26 | EF-RF05- Run Sts | MCC
| UI5 | GND | EF-RF-05 | Fan Trip Status | BI-63 | 27 | EF-RF05- Trip Sts | MCC
| UI6 |  | EF-RF-05 | Fan Auto Status | BI-64 | 28 | EF-RF05- Auto Sts | MCC
| UI7 | GND | EF-RF-06 | Fan Running Status | BI-65 | 29 | EF-RF06- Run Sts | MCC
| UI8 |  | EF-RF-06 | Fan Trip Status | BI-66 | 30 | EF-RF06- Trip Sts | MCC
| UI9 | GND | EF-RF-06 | Fan Auto Status | BI-67 | 31 | EF-RF06- Auto Sts | MCC
| UI10 |  | EF-RF-07 | Fan Running Status | BI-68 | 32 | EF-RF07- Run Sts | MCC
| UI11 | GND | EF-RF-07 | Fan Trip Status | BI-69 | 33 | EF-RF07- Trip Sts | MCC
| UI12 |  | EF-RF-07 | Fan Auto Status | BI-70 | 34 | EF-RF07- Auto Sts | MCC
| UI13 | GND | SEF-RF-07 | Fan ON/OFF Status | BI-71 | 35 | SEF-RF07- ON/OFF Sts | MCC
| UI14 |  | SEF-RF-07 | Fan Trip Status | BI-72 | 36 | SEF-RF07- Trip Sts | MCC
| UI15 | GND | SEF-RF-07 | Fan Proof of Flow | BI-73 | 37 | SEF-RF07- Flow Sts | SWITCH
| UI16 |  | SEF-RF-07 | Fan in AUTO at MCC | BI-74 | 38 | SEF-RF07- Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | MAF-RF-07 | Fan ON/OFF Status | BI-75 | 39 | MAF-RF07- ON/OFF Sts | MCC
| UI2 |  | MAF-RF-07 | Fan Trip Status | BI-76 | 40 | MAF-RF07- Trip Sts | MCC
| UI3 | GND | MAF-RF-07 | Fan Proof of Flow | BI-77 | 41 | MAF-RF07- Flow Sts | SWITCH
| UI4 |  | MAF-RF-07 | Fan in AUTO at MCC | BI-78 | 42 | MAF-RF07- Auto Sts | MCC
| UI5 | GND | PF-RF-03 | Fan Run Status | BI-79 | 43 | PF-RF03- Run Sts | MCC
| UI6 |  | PF-RF-03 | Fan Trip Status | BI-80 | 44 | PF-RF03- Trip Sts | MCC
| UI7 | GND | PF-RF-03 | Fan in OFF Position at MCC | BI-81 | 45 | PF-RF03- OFF Pos Sts | MCC
| UI8 |  |  | SPARE
| UI9 | GND | HRAHU-RF-03 | CHW Valve Position Feedback | AI-83 | 46 | HRAHU-RF03- CHW Valve Fbk | ACTUATOR
| UI10 |  | HRAHU-RF-03 | CHW Return Temperature | AI-84 | 47 | HRAHU-RF03- CHW Ret Temp | SENSOR
| UI11 | GND | HRAHU-RF-03 | Duct Return Temperature | AI-85 | 48 | HRAHU-RF03- Duct Ret Temp | SENSOR
| UI12 |  | HRAHU-RF-04 | CHW Valve Position Feedback | AI-86 | 49 | HRAHU-RF04- CHW Valve Fbk | ACTUATOR
| UI13 | GND | HRAHU-RF-04 | CHW Return Temperature | AI-87 | 50 | HRAHU-RF04- CHW Ret Temp | SENSOR
| UI14 |  | HRAHU-RF-04 | Duct Return Temperature | AI-88 | 51 | HRAHU-RF04- Duct Ret Temp | SENSOR
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-SP-01
DDC-SP-01
Project - BN-01 DDC SIZE - 600 * 600 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | FP-BNSP2-LG-01 | Pump Start/Stop Command | BO-1 | R1 | FP-LG01- Start/Stop Cmd | MCC
| UO2 |  | FP-BNSP2-LG-02 | Pump Start/Stop Command | BO-2 | R2 | FP-LG02- Start/Stop Cmd | MCC
| UO3 | GND | FP-BNSP2-LG-03 | Pump Start/Stop Command | BO-3 | R3 | FP-LG03- Start/Stop Cmd | MCC
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | CRP-BNSP2-LG-01 | Automatic Screen Filter Status | BI-3 | 4 | CRP-LG01- Screen Filter Sts | SWITCH
| UI4 |  | CRP-BNSP2-LG-01 | Strainer Status | BI-4 | 5 | CRP-LG01- Strainer Sts | SWITCH
| UI5 | GND | CRP-BNSP2-LG-01 | Fertilizer Tank Low Level | BI-5 | 6 | CRP-LG01- Tank Low Level | SWITCH
| UI6 |  | CRP-BNSP2-LG-01 | Fertilizer Unit Status | BI-6 | 7 | CRP-LG01- Fertilizer Sts | MCC
| UI7 | GND | CRP-BNSP2-LG-01 | Fertilizer Unit Fault Alarm | BI-7 | 8 | CRP-LG01- Fertilizer Fault | MCC
| UI8 |  | UV.STERIL-SP-01 | Filter Dirty Status | BI-8 | 9 | UV-Steril-SP01- Filter Dirty | SWITCH
| UI9 | GND | CHEM.DOSING-SP-01 | Unit Run Status | BI-9 | 10 | Chem-Dosing-SP01- Run Sts | MCC
| UI10 |  | CHEM.DOSING-SP-01 | Unit Fault Alarm | BI-10 | 11 | Chem-Dosing-SP01- Fault Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | SAND.FILTER-SP-01 | Filter 1 Dirty Status | BI-43 | 12 | Sand-Filter-SP01- F1 Dirty | SWITCH
| UI2 |  | SAND.FILTER-SP-01 | Filter 2 Dirty Status | BI-44 | 13 | Sand-Filter-SP01- F2 Dirty | SWITCH
| UI3 | GND | SAND.FILTER-SP-01 | Filter 3 Dirty Status | BI-45 | 14 | Sand-Filter-SP01- F3 Dirty | SWITCH
| UI4 |  | FP-BNSP2-LG-01 | Pump Trip Status | BI-46 | 15 | FP-LG01- Trip Sts | MCC
| UI5 | GND | FP-BNSP2-LG-01 | Pump Running Status | BI-47 | 16 | FP-LG01- Run Sts | MCC
| UI6 |  | FP-BNSP2-LG-01 | Pump Auto Status | BI-48 | 17 | FP-LG01- Auto Sts | MCC
| UI7 | GND | FP-BNSP2-LG-02 | Pump Trip Status | BI-49 | 18 | FP-LG02- Trip Sts | MCC
| UI8 |  | FP-BNSP2-LG-02 | Pump Running Status | BI-50 | 19 | FP-LG02- Run Sts | MCC
| UI9 | GND | FP-BNSP2-LG-02 | Pump Auto Status | BI-51 | 20 | FP-LG02- Auto Sts | MCC
| UI10 |  | FP-BNSP2-LG-03 | Pump Trip Status | BI-52 | 21 | FP-LG03- Trip Sts | MCC
| UI11 | GND | FP-BNSP2-LG-03 | Pump Running Status | BI-53 | 22 | FP-LG03- Run Sts | MCC
| UI12 |  | FP-BNSP2-LG-03 | Pump Auto Status | BI-54 | 23 | FP-LG03- Auto Sts | MCC
| UI13 | GND | SUMP.PUMP-SP-01 | Duty Pump Status | BI-55 | 24 | Sump-Pump-SP01- Duty Sts | MCC
| UI14 |  | SUMP.PUMP-SP-01 | Duty Pump Trip Status | BI-56 | 25 | Sump-Pump-SP01- Duty Trip Sts | MCC
| UI15 | GND | SUMP.PUMP-SP-01 | Duty Pump Auto Status | BI-57 | 26 | Sump-Pump-SP01- Duty Auto Sts | MCC
| UI16 |  | SUMP.PUMP-SP-01 | Standby Pump Status | BI-58 | 27 | Sump-Pump-SP01- Stby Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | SUMP.PUMP-SP-01 | Standby Pump Trip Status | BI-59 | 28 | Sump-Pump-SP01- Stby Trip Sts | MCC
| UI2 |  | SUMP.PUMP-SP-01 | Standby Pump Auto Status | BI-60 | 29 | Sump-Pump-SP01- Stby Auto Sts | MCC
| UI3 | GND | GRP.SURGE.TANK-SP-01 | Tank Level | AI-61 | 30 | GRP-Tank-SP01- Level | SENSOR
| UI4 |  |  | SPARE
| UI5 | GND |  | SPARE
| UI6 |  |  | SPARE
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| UI9 | GND |  | SPARE
| UI10 |  |  | SPARE
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-SB-01
DDC-SB-01
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - TBD — Controller 1
Controller 1 — DDC-ME521P ¦ All Outputs + DI + 8 AI
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | IDU-GF-02 | Unit Enable/Disable Command | BO-1 | R1 | IDU-GF02- Enable/Disable Cmd | MCC
| UO2 |  | IDU-GF-03 | Unit Enable/Disable Command | BO-2 | R2 | IDU-GF03- Enable/Disable Cmd | MCC
| UO3 | GND | EF-GF-01 | Fan Start/Stop Command | BO-3 | R3 | EF-GF01- Start/Stop Cmd | MCC
| UO4 |  | EF-GF-02 | Fan Start/Stop Command | BO-4 | R4 | EF-GF02- Start/Stop Cmd | MCC
| UO5 | GND | AHU-GF-01 | Supply Fan Start/Stop Command | BO-5 | R5 | AHU-GF01- SF Cmd | MCC
| UO6 |  | AHU-GF-01 | Exhaust Fan Start/Stop Command | BO-6 | R6 | AHU-GF01- EF Cmd | MCC
| UO7 | GND | AHU-GF-01 | Total Recovery Wheel Start/Stop Cmd | BO-7 | R7 | AHU-GF01- HRW Cmd | MCC
| UO8 |  | AHU-GF-01-DX | Supply Fan Start/Stop Command | BO-8 | R8 | AHU-GF01-DX- SF Cmd | MCC
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | IDU-GF-02 | Split Unit Status | BI-3 | 10 | IDU-GF02- Unit Sts | MCC
| UI4 |  | IDU-GF-03 | Split Unit Status | BI-4 | 11 | IDU-GF03- Unit Sts | MCC
| UI5 | GND | EF-GF-01 | Fan Running Status | BI-5 | 12 | EF-GF01- Run Sts | MCC
| UI6 |  | EF-GF-01 | Fan Trip Status | BI-6 | 13 | EF-GF01- Trip Sts | MCC
| UI7 | GND | EF-GF-01 | Fan Auto Status | BI-7 | 14 | EF-GF01- Auto Sts | MCC
| UI8 |  | EF-GF-02 | Fan Running Status | BI-8 | 15 | EF-GF02- Run Sts | MCC
| UI9 | GND | EF-GF-02 | Fan Trip Status | BI-9 | 16 | EF-GF02- Trip Sts | MCC
| UI10 |  | EF-GF-02 | Fan Auto Status | BI-10 | 17 | EF-GF02- Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | AHU-GF-01-DX | CU Start/Stop Command | BO-9 | R9 | AHU-GF01-DX- CU Cmd | MCC
| UO2 |  |  | SPARE
| UO3 | GND | AHU-GF-01 | Supply Fan VFD Control Signal | AO-11 | 9 | AHU-GF01- SF VFD CMD | VFD
| UO4 |  | AHU-GF-01 | CHW Valve Control Signal | AO-12 | 10 | AHU-GF01- CHW CMD | ACTUATOR
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | ATS | On Status of Incomer CB | BI-11 | 18 | ATS- Incomer On Sts | MCC
| UI2 |  | ATS | Off Status of Incomer CB | BI-12 | 19 | ATS- Incomer Off Sts | MCC
| UI3 | GND | ATS | Bypass Position Status | BI-13 | 20 | ATS- Bypass Pos Sts | MCC
| UI4 |  | ATS | Normal/Fault Status | BI-14 | 21 | ATS- Normal Fault Sts | MCC
| UI5 | GND | AHU-GF-01 | Supply Fan Auto Status | BI-15 | 22 | AHU-GF01- SF Auto Sts | MCC
| UI6 |  | AHU-GF-01 | Supply Fan ON/OFF Status | BI-16 | 23 | AHU-GF01- SF ON/OFF Sts | MCC
| UI7 | GND | AHU-GF-01 | Supply Fan Trip Status | BI-17 | 24 | AHU-GF01- SF Trip Sts | MCC
| UI8 |  | AHU-GF-01 | Supply Fan Proof of Flow | BI-18 | 25 | AHU-GF01- SF Flow Sts | SWITCH
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | AHU-GF-01 | Fresh Air Damper Open/Close Status | BI-59 | 26 | AHU-GF01- FA Damper Sts | SWITCH
| UI2 |  | AHU-GF-01 | Return Air Damper Open/Close Status | BI-60 | 27 | AHU-GF01- RA Damper Sts | SWITCH
| UI3 | GND | AHU-GF-01 | Filter Dirty Status | BI-61 | 28 | AHU-GF01- Filter Dirty | SWITCH
| UI4 |  | AHU-GF-01 | Exhaust Fan Auto Status | BI-62 | 29 | AHU-GF01- EF Auto Sts | MCC
| UI5 | GND | AHU-GF-01 | Exhaust Fan ON/OFF Status | BI-63 | 30 | AHU-GF01- EF ON/OFF Sts | MCC
| UI6 |  | AHU-GF-01 | Exhaust Fan Proof of Flow | BI-64 | 31 | AHU-GF01- EF Flow Sts | SWITCH
| UI7 | GND | AHU-GF-01 | Exhaust Fan Trip Status | BI-65 | 32 | AHU-GF01- EF Trip Sts | MCC
| UI8 |  | AHU-GF-01 | Total Recovery Wheel Auto Status | BI-66 | 33 | AHU-GF01- HRW Auto Sts | MCC
| UI9 | GND | AHU-GF-01 | Total Recovery Wheel ON/OFF Status | BI-67 | 34 | AHU-GF01- HRW ON/OFF Sts | MCC
| UI10 |  | AHU-GF-01 | Total Recovery Wheel Fault Status | BI-68 | 35 | AHU-GF01- HRW Fault Sts | MCC
| UI11 | GND | AHU-GF-01-DX | Fresh Air Damper Open/Close Status | BI-69 | 36 | AHU-GF01-DX- FA Damper Sts | SWITCH
| UI12 |  | AHU-GF-01-DX | Return Air Damper Open/Close Status | BI-70 | 37 | AHU-GF01-DX- RA Damper Sts | SWITCH
| UI13 | GND | AHU-GF-01-DX | Pre&Bag Filter Dirty Status | BI-71 | 38 | AHU-GF01-DX- Pre Filter Dirty | SWITCH
| UI14 |  | AHU-GF-01-DX | Supply Fan Run Status |  |  | AHU-GF01-DX- SF Run Sts | MCC
| UI15 | GND | AHU-GF-01-DX | Supply Fan Trip Status | BI-73 | 40 | AHU-GF01-DX- SF Trip Sts | MCC
| UI16 |  | AHU-GF-01-DX | Supply Fan HOA Status | BI-74 | 41 | AHU-GF01-DX- SF HOA Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | AHU-GF-01-DX | CU Run Status | BI-75 | 42 | AHU-GF01-DX- CU Run Sts | MCC
| UI2 |  | SMDB-LV | Incomer Breaker Run | BI-76 | 43 | SMDB-LV- Breaker Run | MCC
| UI3 | GND | SMDB-LV | Incomer Breaker Trip | BI-77 | 44 | SMDB-LV- Breaker Trip | MCC
| UI4 |  | MDB-01 | Main Incomer Run Status | BI-78 | 45 | MDB-01- Incomer Run Sts | MCC
| UI5 | GND | MDB-01 | Main Incomer Trip Status | BI-79 | 46 | MDB-01- Incomer Trip Sts | MCC
| UI6 |  | MDB-02 | Main Incomer Run Status | BI-80 | 47 | MDB-02- Incomer Run Sts | MCC
| UI7 | GND | MDB-02 | Main Incomer Trip Status | BI-81 | 48 | MDB-02- Incomer Trip Sts | MCC
| UI8 |  | MDB-03 | Main Incomer Run Status | BI-82 | 49 | MDB-03- Incomer Run Sts | MCC
| UI9 | GND | MDB-03 | Main Incomer Trip Status | BI-83 | 50 | MDB-03- Incomer Trip Sts | MCC
| UI10 |  | EMDB-LV | Incomer Breaker Run | BI-84 | 51 | EMDB-LV- Breaker Run | MCC
| UI11 | GND | EMDB-LV | Incomer Breaker Trip | BI-85 | 52 | EMDB-LV- Breaker Trip | MCC
| UI12 |  | CAP.BANK-1 | Healthy Status | BI-86 | 53 | Cap-Bank-1- Healthy Sts | MCC
| UI13 | GND | CAP.BANK-2 | Healthy Status | BI-87 | 54 | Cap-Bank-2- Healthy Sts | MCC
| UI14 |  | CAP.BANK-3 | Healthy Status | BI-88 | 55 | Cap-Bank-3- Healthy Sts | MCC
| UI15 | GND | GATE-BARRIER-2 | ON/OFF Status | BI-89 | 56 | Gate-Barrier-2- ON/OFF Sts | MCC
| UI16 |  | GATE-BARRIER-3 | ON/OFF Status | BI-90 | 57 | Gate-Barrier-3- ON/OFF Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | GATE-BARRIER-4 | ON/OFF Status | BI-91 | 57 | Gate-Barrier-4- ON/OFF Sts | MCC
| UI2 |  | GATE-BARRIER-5 | ON/OFF Status | BI-92 | 58 | Gate-Barrier-5- ON/OFF Sts | MCC
| UI3 | GND | GATE-BARRIER-6 | ON/OFF Status | BI-93 | 59 | Gate-Barrier-6- ON/OFF Sts | MCC
| UI4 |  | GATE-BARRIER-7 | ON/OFF Status | BI-94 | 60 | Gate-Barrier-7- ON/OFF Sts | MCC
| UI5 | GND | GATE-BARRIER-8 | ON/OFF Status | BI-95 | 61 | Gate-Barrier-8- ON/OFF Sts | MCC
| UI6 |  | GATE-BARRIER-9 | ON/OFF Status | BI-96 | 62 | Gate-Barrier-9- ON/OFF Sts | MCC
| UI7 | GND | IDU-GF-02 | Space Temperature | BI-97 | 63 | IDU-GF02- Space Temp | SENSOR
| UI8 |  | IDU-GF-03 | Space Temperature | BI-98 | 64 | IDU-GF03- Space Temp | SENSOR
| UI9 | GND | AHU-GF-01 | Supply Fan VFD Feedback | AI-99 | 65 | AHU-GF01- SF VFD Fbk | VFD
| UI10 |  | AHU-GF-01 | CHW Valve Position Feedback | AI-100 | 66 | AHU-GF01- CHW Valve Fbk | ACTUATOR
| UI11 | GND | AHU-GF-01 | CHW Return Temperature | AI-101 | 67 | AHU-GF01- CHW Ret Temp | SENSOR
| UI12 |  | AHU-GF-01 | Duct Return Temperature | AI-102 | 68 | AHU-GF01- Duct Ret Temp | SENSOR
| UI13 | GND | AHU-GF-01 | Return Air Temperature | AI-103 | 69 | AHU-GF01- Return Air Temp | SENSOR
| UI14 |  | AHU-GF-01 | Space Temperature | AI-104 | 70 | AHU-GF01- Space Temp | SENSOR
| UI15 | GND | AHU-GF-01-DX | Off Coil Temperature | AI-105 | 71 | AHU-GF01-DX- Off Coil Temp | SENSOR
UI16
| 24VAC | ~
0VAC
`

## DDC-LG-01
DDC-LG-01
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | IRP-LG-01 | Pump Enable/Disable Command | BO-1 | R1 | IRP-LG01- Enable/Disable Cmd | MCC
| UO2 |  | IRP-LG-02 | Pump Enable/Disable Command | BO-2 | R2 | IRP-LG02- Enable/Disable Cmd | MCC
| UO3 | GND | IRP-LG-03 | Pump Enable/Disable Command | BO-3 | R3 | IRP-LG03- Enable/Disable Cmd | MCC
| UO4 |  | IRP-LG-04 | Pump Enable/Disable Command | BO-4 | R4 | IRP-LG04- Enable/Disable Cmd | MCC
| UO5 | GND | TRP-BNSP2-LG-01 | Pump Start/Stop Command | BO-5 | R5 | TRP-LG01- Start/Stop Cmd | MCC
| UO6 |  | TRP-BNSP2-LG-02 | Pump Start/Stop Command | BO-6 | R6 | TRP-LG02- Start/Stop Cmd | MCC
| UO7 | GND | CRP-BNSP2-LG-01 | Pump Start/Stop Command | BO-7 | R7 | CRP-LG01- Start/Stop Cmd | MCC
| UO8 |  | CRP-BNSP2-LG-02 | Pump Start/Stop Command | BO-8 | R8 | CRP-LG02- Start/Stop Cmd | MCC
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | IRP-LG-01 | Pump ON/OFF Status | BI-3 | 9 | IRP-LG01- ON/OFF Sts | MCC
| UI4 |  | IRP-LG-01 | Pump Trip Status | BI-4 | 10 | IRP-LG01- Trip Sts | MCC
| UI5 | GND | IRP-LG-02 | Pump ON/OFF Status | BI-5 | 11 | IRP-LG02- ON/OFF Sts | MCC
| UI6 |  | IRP-LG-02 | Pump Trip Status | BI-6 | 12 | IRP-LG02- Trip Sts | MCC
| UI7 | GND | IRP-LG-03 | Pump ON/OFF Status | BI-7 | 13 | IRP-LG03- ON/OFF Sts | MCC
| UI8 |  | IRP-LG-03 | Pump Trip Status | BI-8 | 14 | IRP-LG03- Trip Sts | MCC
| UI9 | GND | IRP-LG-04 | Pump ON/OFF Status | BI-9 | 15 | IRP-LG04- ON/OFF Sts | MCC
| UI10 |  | IRP-LG-04 | Pump Trip Status | BI-10 | 16 | IRP-LG04- Trip Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND |  | SPARE
| UO2 |  |  | SPARE
| UO3 | GND |  | SPARE
| UO4 |  |  | SPARE
| UO5 | GND |  | SPARE
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | TRP-BNSP2-LG-01 | Pump ON/OFF Status | BI-11 | 17 | TRP-LG01- ON/OFF Sts | MCC
| UI2 |  | TRP-BNSP2-LG-01 | Pump Trip Status | BI-12 | 18 | TRP-LG01- Trip Sts | MCC
| UI3 | GND | TRP-BNSP2-LG-01 | Pump Auto Status | BI-13 | 19 | TRP-LG01- Auto Sts | MCC
| UI4 |  | TRP-BNSP2-LG-02 | Pump ON/OFF Status | BI-14 | 20 | TRP-LG02- ON/OFF Sts | MCC
| UI5 | GND | TRP-BNSP2-LG-02 | Pump Trip Status | BI-15 | 21 | TRP-LG02- Trip Sts | MCC
| UI6 |  | TRP-BNSP2-LG-02 | Pump Auto Status | BI-16 | 22 | TRP-LG02- Auto Sts | MCC
| UI7 | GND | CRP-BNSP2-LG-01 | Pump Trip Status | BI-17 | 23 | CRP-LG01- Trip Sts | MCC
| UI8 |  | CRP-BNSP2-LG-01 | Pump ON/OFF Status | BI-18 | 24 | CRP-LG01- ON/OFF Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | CRP-BNSP2-LG-01 | Pump HOA Status | BI-59 | 25 | CRP-LG01- HOA Sts | MCC
| UI2 |  | CRP-BNSP2-LG-02 | Pump Trip Status | BI-60 | 26 | CRP-LG02- Trip Sts | MCC
| UI3 | GND | CRP-BNSP2-LG-02 | Pump ON/OFF Status | BI-61 | 27 | CRP-LG02- ON/OFF Sts | MCC
| UI4 |  | CRP-BNSP2-LG-02 | Pump HOA Status | BI-62 | 28 | CRP-LG02- HOA Sts | MCC
| UI5 | GND | SDF-BNSP2-LG-01 | Filter Dirty Status | BI-63 | 29 | SDF-LG01- Filter Dirty | SWITCH
| UI6 |  | SDF-BNSP2-LG-02 | Filter Dirty Status | BI-64 | 30 | SDF-LG02- Filter Dirty | SWITCH
| UI7 | GND | FIRE.PUMP-LG-01 | Electric Pump Run Status | BI-65 | 31 | Fire-Pump- Elec Run Sts | MCC
| UI8 |  | FIRE.PUMP-LG-01 | Electric Pump Fault Status | BI-66 | 32 | Fire-Pump- Elec Fault Sts | MCC
| UI9 | GND | FIRE.PUMP-LG-01 | Diesel Pump Run Status | BI-67 | 33 | Fire-Pump- Diesel Run Sts | MCC
| UI10 |  | FIRE.PUMP-LG-01 | Diesel Pump Fault Status | BI-68 | 34 | Fire-Pump- Diesel Fault Sts | MCC
| UI11 | GND | FIRE.PUMP-LG-01 | Jockey Pump Run Status | BI-69 | 35 | Fire-Pump- Jockey Run Sts | MCC
| UI12 |  | SUMP.PUMP-LG-01 | Duty Pump Run Status | BI-70 | 36 | Sump-LG01- Duty Run Sts | MCC
| UI13 | GND | SUMP.PUMP-LG-01 | Duty Pump Trip Status | BI-71 | 37 | Sump-LG01- Duty Trip Sts | MCC
| UI14 |  | SUMP.PUMP-LG-01 | Duty Pump Auto Status | BI-72 | 38 | Sump-LG01- Duty Auto Sts | MCC
| UI15 | GND | SUMP.PUMP-LG-01 | Standby Pump Run Status | BI-73 | 39 | Sump-LG01- Stby Run Sts | MCC
| UI16 |  | SUMP.PUMP-LG-01 | Standby Pump Trip Status | BI-74 | 40 | Sump-LG01- Stby Trip Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | SUMP.PUMP-LG-01 | Standby Pump Auto Status | BI-75 | 41 | Sump-LG01- Stby Auto Sts | MCC
| UI2 |  | SUMP.PUMP-LG-02 | Duty Pump Run Status | BI-76 | 42 | Sump-LG02- Duty Run Sts | MCC
| UI3 | GND | SUMP.PUMP-LG-02 | Duty Pump Trip Status | BI-77 | 43 | Sump-LG02- Duty Trip Sts | MCC
| UI4 |  | SUMP.PUMP-LG-02 | Duty Pump Auto Status | BI-78 | 44 | Sump-LG02- Duty Auto Sts | MCC
| UI5 | GND | SUMP.PUMP-LG-02 | Standby Pump Run Status | BI-79 | 45 | Sump-LG02- Stby Run Sts | MCC
| UI6 |  | SUMP.PUMP-LG-02 | Standby Pump Trip Status | BI-80 | 46 | Sump-LG02- Stby Trip Sts | MCC
| UI7 | GND | SUMP.PUMP-LG-02 | Standby Pump Auto Status | BI-81 | 47 | Sump-LG02- Stby Auto Sts | MCC
| UI8 |  | MAF-LG-02 | Fan Running Status | BI-82 | 48 | MAF-LG02- Run Sts | MCC
| UI9 | GND | MAF-LG-02 | Fan Trip Status | BI-83 | 49 | MAF-LG02- Trip Sts | MCC
| UI10 |  | MAF-LG-02 | Fan Auto Status | BI-84 | 50 | MAF-LG02- Auto Sts | MCC
| UI11 | GND | EF-LG-02 | Fan Running Status | BI-85 | 51 | EF-LG02- Run Sts | MCC
| UI12 |  | EF-LG-02 | Fan Trip Status | BI-86 | 52 | EF-LG02- Trip Sts | MCC
| UI13 | GND | EF-LG-02 | Fan Auto Status | BI-87 | 53 | EF-LG02- Auto Sts | MCC
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | GRP.TANK-LG-01 | Tank Level | AI-91 | 54 | GRP-Tank-LG01- Level | SENSOR
| UI2 |  | GRP.TANK-LG-02 | Tank Level | AI-92 | 55 | GRP-Tank-LG02- Level | SENSOR
| UI3 | GND | GRP.TANK-LG-03 | Tank Level | AI-93 | 56 | GRP-Tank-LG03- Level | SENSOR
| UI4 |  | RCC.TANK-LG-01 | Tank Level | AI-94 | 57 | RCC-Tank-LG01- Level | SENSOR
| UI5 | GND | RCC.TANK-LG-02 | Tank Level | AI-95 | 58 | RCC-Tank-LG02- Level | SENSOR
| UI6 |  | RCC.TANK-LG-03 | Tank Level | AI-96 | 59 | RCC-Tank-LG03- Level | SENSOR
| UI7 | GND | RCC.TANK-LG-04 | Tank Level | AI-97 | 60 | RCC-Tank-LG04- Level | SENSOR
| UI8 |  | FIRE.PUMP-LG-01 | Static Pressure | AI-98 | 61 | Fire-Pump- Static Pressure | SENSOR
| UI9 | GND |  | SPARE
| UI10 |  |  | SPARE
| UI11 | GND |  | SPARE
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-LG-02
DDC-LG-02
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | JF-LG-01 | Start/Stop Low Speed Command | BO-1 | R1 | JF-LG-01- Start/Stop Cmd | MCC
| UO2 |  | JF-LG-02 | Start/Stop Low Speed Command | BO-2 | R2 | JF-LG-02- Start/Stop Cmd | MCC
| UO3 | GND | JF-LG-03 | Start/Stop Low Speed Command | BO-3 | R3 | JF-LG-03- Start/Stop Cmd | MCC
| UO4 |  | JF-LG-04 | Start/Stop Low Speed Command | BO-4 | R4 | JF-LG-04- Start/Stop Cmd | MCC
| UO5 | GND | JF-LG-05 | Start/Stop Low Speed Command | BO-5 | R5 | JF-LG-05- Start/Stop Cmd | MCC
| UO6 |  | JF-LG-06 | Start/Stop Low Speed Command | BO-6 | R6 | JF-LG-06- Start/Stop Cmd | MCC
| UO7 | GND | JF-LG-07 | Start/Stop Low Speed Command | BO-7 | R7 | JF-LG-07- Start/Stop Cmd | MCC
| UO8 |  | JF-LG-08 | Start/Stop Low Speed Command | BO-8 | R8 | JF-LG-08- Start/Stop Cmd | MCC
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | JF-LG-01 | Run Status | BI-3 | 15 | JF-LG-01- Run Sts | MCC
| UI4 |  | JF-LG-01 | Trip Status | BI-4 | 16 | JF-LG-01- Trip Sts | MCC
| UI5 | GND | JF-LG-01 | Auto Status at MCC | BI-5 | 17 | JF-LG-01- Auto Sts | MCC
| UI6 |  | JF-LG-02 | Run Status | BI-6 | 18 | JF-LG-02- Run Sts | MCC
| UI7 | GND | JF-LG-02 | Trip Status | BI-7 | 19 | JF-LG-02- Trip Sts | MCC
| UI8 |  | JF-LG-02 | Auto Status at MCC | BI-8 | 20 | JF-LG-02- Auto Sts | MCC
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | JF-LG-09 | Start/Stop Low Speed Command | BO-9 | R9 | JF-LG-09- Start/Stop Cmd | MCC
| UO2 |  | JF-LG-10 | Start/Stop Low Speed Command | BO-10 | R10 | JF-LG-10- Start/Stop Cmd | MCC
| UO3 | GND | JF-LG-11 | Start/Stop Low Speed Command | BO-11 | R11 | JF-LG-11- Start/Stop Cmd | MCC
| UO4 |  | JF-LG-12 | Start/Stop Low Speed Command | BO-12 | R12 | JF-LG-12- Start/Stop Cmd | MCC
| UO5 | GND | JF-LG-13 | Start/Stop Low Speed Command | BO-13 | R13 | JF-LG-13- Start/Stop Cmd | MCC
| UO6 |  | IDU-LG-01 | Unit Enable/Disable Command | BO-14 | R14 | IDU-LG01- Enable/Disable Cmd | MCC
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-LG-03 | Run Status | BI-9 | 21 | JF-LG-03- Run Sts | MCC
| UI2 |  | JF-LG-03 | Trip Status | BI-10 | 22 | JF-LG-03- Trip Sts | MCC
| UI3 | GND | JF-LG-03 | Auto Status at MCC | BI-11 | 23 | JF-LG-03- Auto Sts | MCC
| UI4 |  | JF-LG-04 | Run Status | BI-12 | 24 | JF-LG-04- Run Sts | MCC
| UI5 | GND | JF-LG-04 | Trip Status | BI-13 | 25 | JF-LG-04- Trip Sts | MCC
| UI6 |  | JF-LG-04 | Auto Status at MCC | BI-14 | 26 | JF-LG-04- Auto Sts | MCC
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-LG-05 | Run Status | BI-59 | 27 | JF-LG-05- Run Sts | MCC
| UI2 |  | JF-LG-05 | Trip Status | BI-60 | 28 | JF-LG-05- Trip Sts | MCC
| UI3 | GND | JF-LG-05 | Auto Status at MCC | BI-61 | 29 | JF-LG-05- Auto Sts | MCC
| UI4 |  | JF-LG-06 | Run Status | BI-62 | 30 | JF-LG-06- Run Sts | MCC
| UI5 | GND | JF-LG-06 | Trip Status | BI-63 | 31 | JF-LG-06- Trip Sts | MCC
| UI6 |  | JF-LG-06 | Auto Status at MCC | BI-64 | 32 | JF-LG-06- Auto Sts | MCC
| UI7 | GND | JF-LG-07 | Run Status | BI-65 | 33 | JF-LG-07- Run Sts | MCC
| UI8 |  | JF-LG-07 | Trip Status | BI-66 | 34 | JF-LG-07- Trip Sts | MCC
| UI9 | GND | JF-LG-07 | Auto Status at MCC | BI-67 | 35 | JF-LG-07- Auto Sts | MCC
| UI10 |  | JF-LG-08 | Run Status | BI-68 | 36 | JF-LG-08- Run Sts | MCC
| UI11 | GND | JF-LG-08 | Trip Status | BI-69 | 37 | JF-LG-08- Trip Sts | MCC
| UI12 |  | JF-LG-08 | Auto Status at MCC | BI-70 | 38 | JF-LG-08- Auto Sts | MCC
| UI13 | GND | JF-LG-09 | Run Status | BI-71 | 39 | JF-LG-09- Run Sts | MCC
| UI14 |  | JF-LG-09 | Trip Status | BI-72 | 40 | JF-LG-09- Trip Sts | MCC
| UI15 | GND | JF-LG-09 | Auto Status at MCC | BI-73 | 41 | JF-LG-09- Auto Sts | MCC
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-LG-10 | Run Status | BI-75 | 42 | JF-LG-10- Run Sts | MCC
| UI2 |  | JF-LG-10 | Trip Status | BI-76 | 43 | JF-LG-10- Trip Sts | MCC
| UI3 | GND | JF-LG-10 | Auto Status at MCC | BI-77 | 44 | JF-LG-10- Auto Sts | MCC
| UI4 |  | JF-LG-11 | Run Status | BI-78 | 45 | JF-LG-11- Run Sts | MCC
| UI5 | GND | JF-LG-11 | Trip Status | BI-79 | 46 | JF-LG-11- Trip Sts | MCC
| UI6 |  | JF-LG-11 | Auto Status at MCC | BI-80 | 47 | JF-LG-11- Auto Sts | MCC
| UI7 | GND | JF-LG-12 | Run Status | BI-81 | 48 | JF-LG-12- Run Sts | MCC
| UI8 |  | JF-LG-12 | Trip Status | BI-82 | 49 | JF-LG-12- Trip Sts | MCC
| UI9 | GND | JF-LG-12 | Auto Status at MCC | BI-83 | 50 | JF-LG-12- Auto Sts | MCC
| UI10 |  | JF-LG-13 | Run Status | BI-84 | 51 | JF-LG-13- Run Sts | MCC
| UI11 | GND | JF-LG-13 | Trip Status | BI-85 | 52 | JF-LG-13- Trip Sts | MCC
| UI12 |  | JF-LG-13 | Auto Status at MCC | BI-86 | 53 | JF-LG-13- Auto Sts | MCC
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | SMDB-LG-PB | Incomer Breaker Run | BI-91 | 53 | SMDB-LG-PB- Breaker Run | MCC
| UI2 |  | SMDB-LG-PB | Incomer Breaker Trip | BI-92 | 54 | SMDB-LG-PB- Breaker Trip | MCC
| UI3 | GND | ESMDB-LG-PB | Incomer Breaker Run | BI-93 | 55 | ESMDB-LG-PB- Breaker Run | MCC
| UI4 |  | ESMDB-LG-PB | Incomer Breaker Trip | BI-94 | 56 | ESMDB-LG-PB- Breaker Trip | MCC
| UI5 | GND | GATE-BARRIER-1 | ON/OFF Status | BI-95 | 57 | Gate-Barrier-1- ON/OFF Sts | MCC
| UI6 |  | IDU-LG-01 | Split Unit Status | BI-96 | 58 | IDU-LG01- Unit Sts | MCC
| UI7 | GND | SUMP.PUMP-LG-03 | Duty Pump Run Status | BI-97 | 59 | Sump-LG03- Duty Run Sts | MCC
| UI8 |  | SUMP.PUMP-LG-03 | Duty Pump Trip Status | BI-98 | 60 | Sump-LG03- Duty Trip Sts | MCC
| UI9 | GND | SUMP.PUMP-LG-03 | Duty Pump Auto Status | BI-99 | 61 | Sump-LG03- Duty Auto Sts | MCC
| UI10 |  | SUMP.PUMP-LG-03 | Standby Pump Run Status | BI-100 | 62 | Sump-LG03- Stby Run Sts | MCC
| UI11 | GND | SUMP.PUMP-LG-03 | Standby Pump Trip Status | BI-101 | 63 | Sump-LG03- Stby Trip Sts | MCC
| UI12 |  | SUMP.PUMP-LG-03 | Standby Pump Auto Status | BI-102 | 64 | Sump-LG03- Stby Auto Sts | MCC
| UI13 | GND | IDU-LG-01 | Space Temperature | AI-103 | 65 | IDU-LG01- Space Temp | SENSOR
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-LG-03
DDC-LG-03
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | JF-LG-14 | Start/Stop Low Speed Command | BO-1 | R1 | JF-LG-14- Start/Stop Cmd | MCC
| UO2 |  | JF-LG-15 | Start/Stop Low Speed Command | BO-2 | R2 | JF-LG-15- Start/Stop Cmd | MCC
| UO3 | GND | JF-LG-16 | Start/Stop Low Speed Command | BO-3 | R3 | JF-LG-16- Start/Stop Cmd | MCC
| UO4 |  | JF-LG-17 | Start/Stop Low Speed Command | BO-4 | R4 | JF-LG-17- Start/Stop Cmd | MCC
| UO5 | GND | JF-LG-18 | Start/Stop Low Speed Command | BO-5 | R5 | JF-LG-18- Start/Stop Cmd | MCC
| UO6 |  | JF-LG-19 | Start/Stop Low Speed Command | BO-6 | R6 | JF-LG-19- Start/Stop Cmd | MCC
| UO7 | GND | JF-LG-20 | Start/Stop Low Speed Command | BO-7 | R7 | JF-LG-20- Start/Stop Cmd | MCC
| UO8 |  | JF-LG-21 | Start/Stop Low Speed Command | BO-8 | R8 | JF-LG-21- Start/Stop Cmd | MCC
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | JF-LG-14 | Run Status | BI-3 | 14 | JF-LG-14- Run Sts | MCC
| UI4 |  | JF-LG-14 | Trip Status | BI-4 | 15 | JF-LG-14- Trip Sts | MCC
| UI5 | GND | JF-LG-14 | Auto Status at MCC | BI-5 | 16 | JF-LG-14- Auto Sts | MCC
| UI6 |  | JF-LG-15 | Run Status | BI-6 | 17 | JF-LG-15- Run Sts | MCC
| UI7 | GND | JF-LG-15 | Trip Status | BI-7 | 18 | JF-LG-15- Trip Sts | MCC
| UI8 |  | JF-LG-15 | Auto Status at MCC | BI-8 | 19 | JF-LG-15- Auto Sts | MCC
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | JF-LG-22 | Start/Stop Low Speed Command | BO-9 | R9 | JF-LG-22- Start/Stop Cmd | MCC
| UO2 |  | JF-LG-23 | Start/Stop Low Speed Command | BO-10 | R10 | JF-LG-23- Start/Stop Cmd | MCC
| UO3 | GND | JF-LG-24 | Start/Stop Low Speed Command | BO-11 | R11 | JF-LG-24- Start/Stop Cmd | MCC
| UO4 |  | JF-LG-25 | Start/Stop Low Speed Command | BO-12 | R12 | JF-LG-25- Start/Stop Cmd | MCC
| UO5 | GND | JF-LG-26 | Start/Stop Low Speed Command | BO-13 | R13 | JF-LG-26- Start/Stop Cmd | MCC
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-LG-16 | Run Status | BI-9 | 20 | JF-LG-16- Run Sts | MCC
| UI2 |  | JF-LG-16 | Trip Status | BI-10 | 21 | JF-LG-16- Trip Sts | MCC
| UI3 | GND | JF-LG-16 | Auto Status at MCC | BI-11 | 22 | JF-LG-16- Auto Sts | MCC
| UI4 |  | JF-LG-17 | Run Status | BI-12 | 23 | JF-LG-17- Run Sts | MCC
| UI5 | GND | JF-LG-17 | Trip Status | BI-13 | 24 | JF-LG-17- Trip Sts | MCC
| UI6 |  | JF-LG-17 | Auto Status at MCC | BI-14 | 25 | JF-LG-17- Auto Sts | MCC
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-LG-18 | Run Status | BI-59 | 26 | JF-LG-18- Run Sts | MCC
| UI2 |  | JF-LG-18 | Trip Status | BI-60 | 27 | JF-LG-18- Trip Sts | MCC
| UI3 | GND | JF-LG-18 | Auto Status at MCC | BI-61 | 28 | JF-LG-18- Auto Sts | MCC
| UI4 |  | JF-LG-19 | Run Status | BI-62 | 29 | JF-LG-19- Run Sts | MCC
| UI5 | GND | JF-LG-19 | Trip Status | BI-63 | 30 | JF-LG-19- Trip Sts | MCC
| UI6 |  | JF-LG-19 | Auto Status at MCC | BI-64 | 31 | JF-LG-19- Auto Sts | MCC
| UI7 | GND | JF-LG-20 | Run Status | BI-65 | 32 | JF-LG-20- Run Sts | MCC
| UI8 |  | JF-LG-20 | Trip Status | BI-66 | 33 | JF-LG-20- Trip Sts | MCC
| UI9 | GND | JF-LG-20 | Auto Status at MCC | BI-67 | 34 | JF-LG-20- Auto Sts | MCC
| UI10 |  | JF-LG-21 | Run Status | BI-68 | 35 | JF-LG-21- Run Sts | MCC
| UI11 | GND | JF-LG-21 | Trip Status | BI-69 | 36 | JF-LG-21- Trip Sts | MCC
| UI12 |  | JF-LG-21 | Auto Status at MCC | BI-70 | 37 | JF-LG-21- Auto Sts | MCC
| UI13 | GND | JF-LG-22 | Run Status | BI-71 | 38 | JF-LG-22- Run Sts | MCC
| UI14 |  | JF-LG-22 | Trip Status | BI-72 | 39 | JF-LG-22- Trip Sts | MCC
| UI15 | GND | JF-LG-22 | Auto Status at MCC | BI-73 | 40 | JF-LG-22- Auto Sts | MCC
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-LG-23 | Run Status | BI-75 | 41 | JF-LG-23- Run Sts | MCC
| UI2 |  | JF-LG-23 | Trip Status | BI-76 | 42 | JF-LG-23- Trip Sts | MCC
| UI3 | GND | JF-LG-23 | Auto Status at MCC | BI-77 | 43 | JF-LG-23- Auto Sts | MCC
| UI4 |  | JF-LG-24 | Run Status | BI-78 | 44 | JF-LG-24- Run Sts | MCC
| UI5 | GND | JF-LG-24 | Trip Status | BI-79 | 45 | JF-LG-24- Trip Sts | MCC
| UI6 |  | JF-LG-24 | Auto Status at MCC | BI-80 | 46 | JF-LG-24- Auto Sts | MCC
| UI7 | GND | JF-LG-25 | Run Status | BI-81 | 47 | JF-LG-25- Run Sts | MCC
| UI8 |  | JF-LG-25 | Trip Status | BI-82 | 48 | JF-LG-25- Trip Sts | MCC
| UI9 | GND | JF-LG-25 | Auto Status at MCC | BI-83 | 49 | JF-LG-25- Auto Sts | MCC
| UI10 |  | JF-LG-26 | Run Status | BI-84 | 50 | JF-LG-26- Run Sts | MCC
| UI11 | GND | JF-LG-26 | Trip Status | BI-85 | 51 | JF-LG-26- Trip Sts | MCC
| UI12 |  | JF-LG-26 | Auto Status at MCC | BI-86 | 52 | JF-LG-26- Auto Sts | MCC
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | SUMP.PUMP-LG-02 | Duty Pump Run Status | BI-91 | 53 | Sump-LG02- Duty Run Sts | MCC
| UI2 |  | SUMP.PUMP-LG-02 | Duty Pump Trip Status | BI-92 | 54 | Sump-LG02- Duty Trip Sts | MCC
| UI3 | GND | SUMP.PUMP-LG-02 | Duty Pump Auto Status | BI-93 | 55 | Sump-LG02- Duty Auto Sts | MCC
| UI4 |  | SUMP.PUMP-LG-02 | Standby Pump Run Status | BI-94 | 56 | Sump-LG02- Stby Run Sts | MCC
| UI5 | GND | SUMP.PUMP-LG-02 | Standby Pump Trip Status | BI-95 | 57 | Sump-LG02- Stby Trip Sts | MCC
| UI6 |  | SUMP.PUMP-LG-02 | Standby Pump Auto Status | BI-96 | 58 | Sump-LG02- Stby Auto Sts | MCC
| UI7 | GND | SAND.TRAP-LG-01 | Common Fault Alarm | BI-97 | 59 | Sand-Trap-LG01- Fault Sts | MCC
| UI8 |  | SMDB-EV-PB | Incomer Breaker Run | BI-98 | 60 | SMDB-EV-PB- Breaker Run | MCC
| UI9 | GND | SMDB-EV-PB | Incomer Breaker Trip | BI-99 | 61 | SMDB-EV-PB- Breaker Trip | MCC
| UI10 |  |  | SPARE
| UI11 | GND | TELECOM-ROOM | Space Temperature | AI-101 | 62 | Telecom-Room- Space Temp | SENSOR
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-UG-01
DDC-UG-01
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | JF-UG-08 | Start/Stop Low Speed Command | BO-1 | R1 | JF-UG-08- Start/Stop Cmd | MCC
| UO2 |  | JF-UG-10 | Start/Stop Low Speed Command | BO-2 | R2 | JF-UG-10- Start/Stop Cmd | MCC
| UO3 | GND | JF-UG-12 | Start/Stop Low Speed Command | BO-3 | R3 | JF-UG-12- Start/Stop Cmd | MCC
| UO4 |  | JF-UG-13 | Start/Stop Low Speed Command | BO-4 | R4 | JF-UG-13- Start/Stop Cmd | MCC
| UO5 | GND | JF-UG-14 | Start/Stop Low Speed Command | BO-5 | R5 | JF-UG-14- Start/Stop Cmd | MCC
| UO6 |  | JF-UG-15 | Start/Stop Low Speed Command | BO-6 | R6 | JF-UG-15- Start/Stop Cmd | MCC
| UO7 | GND | JF-UG-16 | Start/Stop Low Speed Command | BO-7 | R7 | JF-UG-16- Start/Stop Cmd | MCC
| UO8 |  | JF-UG-17 | Start/Stop Low Speed Command | BO-8 | R8 | JF-UG-17- Start/Stop Cmd | MCC
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | JF-UG-08 | Run Status | BI-3 | 18 | JF-UG-08- Run Sts | MCC
| UI4 |  | JF-UG-08 | Trip Status | BI-4 | 19 | JF-UG-08- Trip Sts | MCC
| UI5 | GND | JF-UG-08 | Auto Status at MCC | BI-5 | 20 | JF-UG-08- Auto Sts | MCC
| UI6 |  | JF-UG-10 | Run Status | BI-6 | 21 | JF-UG-10- Run Sts | MCC
| UI7 | GND | JF-UG-10 | Trip Status | BI-7 | 22 | JF-UG-10- Trip Sts | MCC
| UI8 |  | JF-UG-10 | Auto Status at MCC | BI-8 | 23 | JF-UG-10- Auto Sts | MCC
| UI7 | GND | JF-UG-12 | Run Status | BI-9 | 24 | JF-UG-12- Run Sts | MCC
| UI8 |  | JF-UG-12 | Trip Status | BI-10 | 25 | JF-UG-12- Trip Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | JF-UG-18 | Start/Stop Low Speed Command | BO-9 | R9 | JF-UG-18- Start/Stop Cmd | MCC
| UO2 |  | JF-UG-19 | Start/Stop Low Speed Command | BO-10 | R10 | JF-UG-19- Start/Stop Cmd | MCC | 8
| UO3 | GND | JF-UG-20 | Start/Stop Low Speed Command | BO-11 | R11 | JF-UG-20- Start/Stop Cmd | MCC | 10
| UO4 |  | JF-UG-21 | Start/Stop Low Speed Command | BO-12 | R12 | JF-UG-21- Start/Stop Cmd | MCC | 12
| UO5 | GND | JF-UG-22 | Start/Stop Low Speed Command | BO-13 | R13 | JF-UG-22- Start/Stop Cmd | MCC | 13
| UO6 |  | JF-UG-23 | Start/Stop Low Speed Command | BO-14 | R14 | JF-UG-23- Start/Stop Cmd | MCC | 14
| UO7 | GND | JF-UG-24 | Start/Stop Low Speed Command | BO-15 | R15 | JF-UG-24- Start/Stop Cmd | MCC | 15
| UO8 |  | JF-UG-25 | Start/Stop Low Speed Command | BO-16 | R16 | JF-UG-25- Start/Stop Cmd | MCC | 16
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC | 17
|  |  | System | Point Description |  |  |  |  | 18
| UI1 | GND | JF-UG-12 | Auto Status at MCC | BI-11 | 26 | JF-UG-12- Auto Sts | MCC | 19
| UI2 |  | JF-UG-13 | Run Status | BI-12 | 27 | JF-UG-13- Run Sts | MCC | 20
| UI3 | GND | JF-UG-13 | Trip Status | BI-13 | 28 | JF-UG-13- Trip Sts | MCC | 21
| UI4 |  | JF-UG-13 | Auto Status at MCC | BI-14 | 29 | JF-UG-13- Auto Sts | MCC | 22
| UI5 | GND | JF-UG-14 | Run Status | BI-15 | 30 | JF-UG-14- Run Sts | MCC | 23
| UI6 |  | JF-UG-14 | Trip Status | BI-16 | 31 | JF-UG-14- Trip Sts | MCC | 24
| UI7 | GND | JF-UG-14 | Auto Status at MCC | BI-17 | 32 | JF-UG-14- Auto Sts | MCC | 25
| UI8 |  | JF-UG-15 | Run Status | BI-18 | 33 | JF-UG-15- Run Sts | MCC | 26
| 24VAC | ~
0VAC
Module-FBM-8I8O (2)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | JF-UG-26 | Start/Stop Low Speed Command | BO-17 | R17 | JF-UG-26- Start/Stop Cmd | MCC
UO2
| UO3 | GND
UO4
| UO5 | GND
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-UG-15 | Trip Status | BI-19 | 34 | JF-UG-15- Trip Sts | MCC
| UI2 |  | JF-UG-15 | Auto Status at MCC | BI-20 | 35 | JF-UG-15- Auto Sts | MCC
| UI3 | GND | JF-UG-16 | Run Status | BI-21 | 36 | JF-UG-16- Run Sts | MCC
| UI4 |  | JF-UG-16 | Trip Status | BI-22 | 37 | JF-UG-16- Trip Sts | MCC
| UI5 | GND | JF-UG-16 | Auto Status at MCC | BI-23 | 38 | JF-UG-16- Auto Sts | MCC
| UI6 |  | JF-UG-17 | Run Status | BI-24 | 39 | JF-UG-17- Run Sts | MCC
| UI7 | GND | JF-UG-17 | Trip Status | BI-25 | 40 | JF-UG-17- Trip Sts | MCC
| UI8 |  | JF-UG-17 | Auto Status at MCC | BI-26 | 41 | JF-UG-17- Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (3)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-UG-18 | Run Status | BI-75 | 42 | JF-UG-18- Run Sts | MCC
| UI2 |  | JF-UG-18 | Trip Status | BI-76 | 43 | JF-UG-18- Trip Sts | MCC
| UI3 | GND | JF-UG-18 | Auto Status at MCC | BI-77 | 44 | JF-UG-18- Auto Sts | MCC
| UI4 |  | JF-UG-19 | Run Status | BI-78 | 45 | JF-UG-19- Run Sts | MCC
| UI5 | GND | JF-UG-19 | Trip Status | BI-79 | 46 | JF-UG-19- Trip Sts | MCC
| UI6 |  | JF-UG-19 | Auto Status at MCC | BI-80 | 47 | JF-UG-19- Auto Sts | MCC
| UI7 | GND | JF-UG-20 | Run Status | BI-81 | 48 | JF-UG-20- Auto Sts | MCC
| UI8 |  | JF-UG-20 | Trip Status | BI-82 | 49 | JF-UG-20- Auto Sts | MCC
| UI9 | GND | JF-UG-20 | Auto Status at MCC | BI-83 | 50 | JF-UG-20- Auto Sts | MCC
| UI10 |  | JF-UG-21 | Run Status | BI-84 | 51 | JF-UG-21- Auto Sts | MCC
| UI11 | GND | JF-UG-21 | Trip Status | BI-85 | 52 | JF-UG-21- Auto Sts | MCC
| UI12 |  | JF-UG-21 | Auto Status at MCC | BI-86 | 53 | JF-UG-21- Auto Sts | MCC
| UI13 | GND | JF-UG-22 | Run Status | BI-87 | 54 | JF-UG-22- Auto Sts | MCC
| UI14 |  | JF-UG-22 | Trip Status | BI-88 | 55 | JF-UG-22- Auto Sts | MCC
| UI15 | GND | JF-UG-22 | Auto Status at MCC | BI-89 | 56 | JF-UG-22- Auto Sts | MCC
| UI16 |  | JF-UG-23 | Run Status | BI-90 | 57 | JF-UG-23- Auto Sts | MCC
| 24VAC | ~
0VAC
Module-FBM-16I (4)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-UG-23 | Trip Status | BI-91 | 58 | JF-UG-23- Trip Sts | MCC
| UI2 |  | JF-UG-23 | Auto Status at MCC | BI-92 | 59 | JF-UG-23- Auto Sts | MCC
| UI3 | GND | JF-UG-24 | Run Status | BI-93 | 60 | JF-UG-24- Run Sts | MCC
| UI4 |  | JF-UG-24 | Trip Status | BI-94 | 61 | JF-UG-24- Trip Sts | MCC
| UI5 | GND | JF-UG-24 | Auto Status at MCC | BI-95 | 62 | JF-UG-24- Auto Sts | MCC
| UI6 |  | JF-UG-25 | Run Status | BI-96 | 63 | JF-UG-25- Run Sts | MCC
| UI7 | GND | JF-UG-25 | Trip Status | BI-97 | 64 | JF-UG-25- Trip Sts | MCC
| UI8 |  | JF-UG-25 | Auto Status at MCC | BI-98 | 65 | JF-UG-25- Auto Sts | MCC
| UI9 | GND | JF-UG-26 | Run Status | BI-99 | 66 | JF-UG-26- Run Sts | MCC
| UI10 |  | JF-UG-26 | Trip Status | BI-100 | 67 | JF-UG-26- Trip Sts | MCC
| UI11 | GND | JF-UG-26 | Auto Status at MCC | BI-101 | 68 | JF-UG-26- Auto Sts | MCC
| UI12 |  |  | SPARE
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC

## DDC-UG-02
DDC-UG-02
Project - BN-01 DDC SIZE - 1000 * 800 DDC IP - BACNET ID - TBD
Controller — DDC-ME521P
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | JF-UG-14 | Start/Stop Low Speed Command | BO-1 | R1 | JF-UG-14- Start/Stop Cmd | MCC
| UO2 |  | JF-UG-15 | Start/Stop Low Speed Command | BO-2 | R2 | JF-UG-15- Start/Stop Cmd | MCC
| UO3 | GND | JF-UG-16 | Start/Stop Low Speed Command | BO-3 | R3 | JF-UG-16- Start/Stop Cmd | MCC
| UO4 |  | JF-UG-17 | Start/Stop Low Speed Command | BO-4 | R4 | JF-UG-17- Start/Stop Cmd | MCC
| UO5 | GND | JF-UG-18 | Start/Stop Low Speed Command | BO-5 | R5 | JF-UG-18- Start/Stop Cmd | MCC
| UO6 |  | JF-UG-19 | Start/Stop Low Speed Command | BO-6 | R6 | JF-UG-19- Start/Stop Cmd | MCC
| UO7 | GND | JF-UG-20 | Start/Stop Low Speed Command | BO-7 | R7 | JF-UG-20- Start/Stop Cmd | MCC
| UO8 |  | JF-UG-21 | Start/Stop Low Speed Command | BO-8 | R8 | JF-UG-21- Start/Stop Cmd | MCC
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI3 | GND | JF-UG-14 | Run Status | BI-3 | 14 | JF-UG-14- Run Sts | MCC
| UI4 |  | JF-UG-14 | Trip Status | BI-4 | 15 | JF-UG-14- Trip Sts | MCC
| UI5 | GND | JF-UG-14 | Auto Status at MCC | BI-5 | 16 | JF-UG-14- Auto Sts | MCC
| UI6 |  | JF-UG-15 | Run Status | BI-6 | 17 | JF-UG-15- Run Sts | MCC
| UI7 | GND | JF-UG-15 | Trip Status | BI-7 | 18 | JF-UG-15- Trip Sts | MCC
| UI8 |  | JF-UG-15 | Auto Status at MCC | BI-8 | 19 | JF-UG-15- Auto Sts | MCC
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-8I8O (1)
| PIN | COM | UNIVERSAL OUTPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UO1 | GND | JF-UG-22 | Start/Stop Low Speed Command | BO-9 | R9 | JF-UG-22- Start/Stop Cmd | MCC
| UO2 |  | JF-UG-23 | Start/Stop Low Speed Command | BO-10 | R10 | JF-UG-23- Start/Stop Cmd | MCC
| UO3 | GND | JF-UG-24 | Start/Stop Low Speed Command | BO-11 | R11 | JF-UG-24- Start/Stop Cmd | MCC
| UO4 |  | JF-UG-25 | Start/Stop Low Speed Command | BO-12 | R12 | JF-UG-25- Start/Stop Cmd | MCC
| UO5 | GND | JF-UG-26 | Start/Stop Low Speed Command | BO-13 | R13 | JF-UG-26- Start/Stop Cmd | MCC
| UO6 |  |  | SPARE
| UO7 | GND |  | SPARE
| UO8 |  |  | SPARE
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-UG-16 | Run Status | BI-9 | 20 | JF-UG-16- Run Sts | MCC
| UI2 |  | JF-UG-16 | Trip Status | BI-10 | 21 | JF-UG-16- Trip Sts | MCC
| UI3 | GND | JF-UG-16 | Auto Status at MCC | BI-11 | 22 | JF-UG-16- Auto Sts | MCC
| UI4 |  | JF-UG-17 | Run Status | BI-12 | 23 | JF-UG-17- Run Sts | MCC
| UI5 | GND | JF-UG-17 | Trip Status | BI-13 | 24 | JF-UG-17- Trip Sts | MCC
| UI6 |  | JF-UG-17 | Auto Status at MCC | BI-14 | 25 | JF-UG-17- Auto Sts | MCC
| UI7 | GND |  | SPARE
| UI8 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (1)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-UG-18 | Run Status | BI-59 | 26 | JF-UG-18- Run Sts | MCC
| UI2 |  | JF-UG-18 | Trip Status | BI-60 | 27 | JF-UG-18- Trip Sts | MCC
| UI3 | GND | JF-UG-18 | Auto Status at MCC | BI-61 | 28 | JF-UG-18- Auto Sts | MCC
| UI4 |  | JF-UG-19 | Run Status | BI-62 | 29 | JF-UG-19- Run Sts | MCC
| UI5 | GND | JF-UG-19 | Trip Status | BI-63 | 30 | JF-UG-19- Trip Sts | MCC
| UI6 |  | JF-UG-19 | Auto Status at MCC | BI-64 | 31 | JF-UG-19- Auto Sts | MCC
| UI7 | GND | JF-UG-20 | Run Status | BI-65 | 32 | JF-UG-20- Run Sts | MCC
| UI8 |  | JF-UG-20 | Trip Status | BI-66 | 33 | JF-UG-20- Trip Sts | MCC
| UI9 | GND | JF-UG-20 | Auto Status at MCC | BI-67 | 34 | JF-UG-20- Auto Sts | MCC
| UI10 |  | JF-UG-21 | Run Status | BI-68 | 35 | JF-UG-21- Run Sts | MCC
| UI11 | GND | JF-UG-21 | Trip Status | BI-69 | 36 | JF-UG-21- Trip Sts | MCC
| UI12 |  | JF-UG-21 | Auto Status at MCC | BI-70 | 37 | JF-UG-21- Auto Sts | MCC
| UI13 | GND | JF-UG-22 | Run Status | BI-71 | 38 | JF-UG-22- Run Sts | MCC
| UI14 |  | JF-UG-22 | Trip Status | BI-72 | 39 | JF-UG-22- Trip Sts | MCC
| UI15 | GND | JF-UG-22 | Auto Status at MCC | BI-73 | 40 | JF-UG-22- Auto Sts | MCC
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC
Module-FBM-16I (2)
| PIN | COM | UNIVERSAL INPUT |  | Object Instance FOR SOFTWARE USE | CABLE NUMBER | CABLE DESCRIPTION | SENSOR/MCC
|  |  | System | Point Description
| UI1 | GND | JF-UG-23 | Run Status | BI-75 | 41 | JF-UG-23- Run Sts | MCC
| UI2 |  | JF-UG-23 | Trip Status | BI-76 | 42 | JF-UG-23- Trip Sts | MCC
| UI3 | GND | JF-UG-23 | Auto Status at MCC | BI-77 | 43 | JF-UG-23- Auto Sts | MCC
| UI4 |  | JF-UG-24 | Run Status | BI-78 | 44 | JF-UG-24- Run Sts | MCC
| UI5 | GND | JF-UG-24 | Trip Status | BI-79 | 45 | JF-UG-24- Trip Sts | MCC
| UI6 |  | JF-UG-24 | Auto Status at MCC | BI-80 | 46 | JF-UG-24- Auto Sts | MCC
| UI7 | GND | JF-UG-25 | Run Status | BI-81 | 47 | JF-UG-25- Run Sts | MCC
| UI8 |  | JF-UG-25 | Trip Status | BI-82 | 48 | JF-UG-25- Trip Sts | MCC
| UI9 | GND | JF-UG-25 | Auto Status at MCC | BI-83 | 49 | JF-UG-25- Auto Sts | MCC
| UI10 |  | JF-UG-26 | Run Status | BI-84 | 50 | JF-UG-26- Run Sts | MCC
| UI11 | GND | JF-UG-26 | Trip Status | BI-85 | 51 | JF-UG-26- Trip Sts | MCC
| UI12 |  | JF-UG-26 | Auto Status at MCC | BI-86 | 52 | JF-UG-26- Auto Sts | MCC
| UI13 | GND |  | SPARE
| UI14 |  |  | SPARE
| UI15 | GND |  | SPARE
| UI16 |  |  | SPARE
| 24VAC | ~
0VAC