## As per Site
Quantity | LOCATION OF EQUIPMENT | Required Points
| Start From Here | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
| TOTAL (1 System) | 0 | 0 | 0 | 0 | 0
| TOTAL | 0 | 0 | 0 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points | [8 empty] | Remarks
| DDC-GF-01 (ELECTRICAL ROOM Z4PT3) | DI | DO | AI | AO | SI | Cable Pulling | Cable Continuity test | Cable Termination | Functionality Test
3 | Ceiling Air Handling Unit
CAHU-4,5,6
| Supply temperature & humidity |  |  | 6 |  |  | ✔️ | ✔️ | ✔️
| Return air/Space temperature |  |  | 3 |  |  | ✔️ | ✔️ | ✔️
| Carbon dioxide level |  |  | 3 |  |  | ✔️ | ✔️ | ✔️
| Supply fan start/stop command |  | 3 |  |  |  | ✔️ | ✔️ | ✔️
| Supply fan ON/OFF status | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
| Supply fan trip status | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
| Supply fan proof of flow | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
| Chilled water valve position command & feedback |  |  | 3 | 3 |  | ✔️ | ✔️ | ✔️
| Chilled water return temperature |  |  | 3 |  |  | ✔️ | ✔️ | ✔️
1 | SMDB
SMDB-GF-MP
| Run status of CB | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| Trip status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
1 | Outdoor Pre Insulated Pipe Leak Detection System
| Leak Detection Alarm | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| TOTAL | 12 | 3 | 18 | 3 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-GF-02 (EQUIPMENT ROOM - Z4PT1 ) | DI | DO | AI | AO | SI | Cable Pulling | Cable Continuity test | Cable Termination | Functionality Test
3 | Ceiling Air Handling Unit
CAHU-1,2,3
| Supply temperature & humidity |  |  | 6 |  |  | ✔️ | ✔️ | ✔️
| Return air/Space temperature |  |  | 3 |  |  | ✔️ | ✔️ | ✔️
| Carbon dioxide level |  |  | 3 |  |  | ✔️ | ✔️ | ✔️
| Supply fan start/stop command |  | 3 |  |  |  | ✔️ | ✔️ | ✔️
| Supply fan ON/OFF status | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
| Supply fan trip status | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
| Supply fan proof of flow | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
| Chilled water valve position command & feedback |  |  | 3 | 3 |  | ✔️ | ✔️ | ✔️
| Chilled water return temperature |  |  | 3 |  |  | ✔️ | ✔️ | ✔️
2 | DX Unit
IDU-GF-04(UPS Room),05 (SEC. Room)
| Space Temperature |  |  | 2 |  |  | ✔️ | ✔️ | ✔️
| Unit enable/disable command |  | 2 |  |  |  | ✔️ | ✔️ | ✔️
| Split unit status | 2 |  |  |  |  | ✔️ | ✔️ | ✔️
3 | CCTV RACK
| Main On/Off status | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
| UPS On/Off Status | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
1 | PAVA System
| Unit on/off status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| Normal/fault status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| TOTAL | 19 | 5 | 20 | 3 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-GF-03 (FCC ROOM - Z1PT2 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | PAVA System
| Unit on/off status | 1
| Normal/fault status | 1
1 | Disabled Toilet Alarm
| Unit on/off status | 1
| Common fault alarm | 1
6 | Gate Barrier - 1/1 , 1/2 , 2/1 , 2/2 , 3/1, 3/2
| Unit on/off status | 6
1 | DX Unit
IDU-GF-01 (FCC Room)
| Space Temperature |  |  | 1
| Unit enable/disable command |  | 1
| Split unit status | 1
1 | SMDB
SMDB-EV-EXT
| Run status of CB | 1
| Trip status | 1
| TOTAL | 13 | 1 | 1 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-GF-04 (STORAGE ROOM - Z1PT1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | SMDB
SMDB-GF-04
| Run status of CB | 1
| Trip status | 1
1 | ESMDB
ESMDB-GF-4
| Run status of CB | 1
| Trip status | 1
1 | SMDB
SMDB-FF-04
| Run status of CB | 1
| Trip status | 1
1 | Lift-4
| Run status | 1
| Cabin Call Alarm | 1
| Fault Status | 1
3 | Air Curtain - AC-01,AC-02,AC-05
| Unit normal/fault | 3
| TOTAL | 12 | 0 | 0 | 0 | 0
QTY | LOCATION OF EQUIPMENT | Required Points
| DDC-GF-05 (ELECTRICAL ROOM - Z3PT2) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
3 | SMDB
SMDB-FF-01,GF-01,SF-01
| Run status of CB | 3
| Trip status | 3
1 | ESMDB
ESMDB-GF-01
| Run status of CB | 1
| Trip status | 1
1 | USMDB
USMDB-GF-01
| Run status of CB | 1
| Trip status | 1
1 | DX Unit
IDU-GF-06 (UPS Room)
| Space Temperature |  |  | 1
| Unit enable/disable command |  | 1
| Split unit status | 1
1 | SERVER ROOM - Leak Detection System
| Leak Detection System | 1
2 | Master Clock System
| Common fault alarm | 2
| Unit on/off status | 2
1 | Lift-1
| Run status | 1
| Cabin Call Alarm | 1
| Fault Status | 1
| TOTAL | 19 | 1 | 1 | 0 | 0
QTY | LOCATION OF EQUIPMENT | Required Points
| DDC-FF-01 (ELECTRICAL ROOM - Z3PT3) | DI | DO | AI | AO | SI | Cable Pulling | Cable Continuity test | Cable Termination | Functionality Test
3 | SMDB
SMDB-FF-02,SF-02,GF-2
| Run status of CB | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
| Trip status | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
1 | ESMDB
ESMDB-GF-02
| Run status of CB | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| Trip status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
1 | Lift-2
| Run status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| Cabin Call Alarm | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| Fault Status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
1 | DX Unit
IDU-GF-07 (GSM Room)
| Space Temperature |  |  | 1 |  |  | ✔️ | ✔️ | ✔️
| Unit enable/disable command |  | 1 |  |  |  | ✔️ | ✔️ | ✔️
| Split unit status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| TOTAL | 12 | 1 | 1 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points |  |  |  |  | Checklist |  |  |  | Remarks
| DDC-FF-02 (ELECTRICAL ROOM -Z2PT3 ) | DI | DO | AI | AO | SI | Cable Pulling | Cable Continuity test | Cable Termination | Functionality Test
3 | Air Curtain - AC-03,04,06
| Unit normal/fault | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
3 | SMDB
SMDB-GF-03,FF-03,SF-03
| Run status of CB | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
| Trip status | 3 |  |  |  |  | ✔️ | ✔️ | ✔️
1 | ESMDB
ESMDB-GF-03
| Run status of CB | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| Trip status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
1 | Lift-3
| Run status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| Cabin Call Alarm | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| Fault Status | 1 |  |  |  |  | ✔️ | ✔️ | ✔️
| TOTAL | 14 | 0 | 0 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-SF-01 (ROOF -Z4 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Air Handling Unit - Swimming Pool (AHU-SF-02)
| Supply temperature & humidity |  |  | 2
| Return/Space air temperature |  |  | 1
| Fresh air temperature & humidity |  |  | 2
| Supply fan start/stop command |  | 1
| Supply fan ON/OFF status | 1
| Supply fan trip status | 1
| Supply fan auto position | 1
| Supply fan proof of flow | 1
| Supply fan VFD command & feedback |  |  | 1 | 1
| Dampers open/close status | 1
| Pre & Bag filter dirty status | 1
| Chilled water valve position command & feedback |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Smoke detection |  |  |  |  | 1
| Exhaust fan VFD command & feedback |  |  | 1 | 1
| Exhaust fan start/stop command |  | 1
| Exhaust fan ON/OFF status | 1
| Exhaust fan trip status | 1
| Exhaust fan auto position | 1
| Exhaust fan Proof of flow | 1
| Exhaust temperature & humidity |  |  | 2
| Total Recovery wheel start/stop command |  | 1
| Total Recovery wheel on/off status | 1
| Total Recovery wheel fault status | 1
| Fresh air wheel leaving temperature & humidity |  |  | 2
| Carbon dioxide level - Duct |  |  | 1
| Carbon dioxide level- Space |  |  | 1
| Return Air Temp and Humidity (Duct & wall) |  |  | 4
| Wall mount Thermostat |  |  | 1
| Reheat valve command and feedback |  |  | 1 | 1
1 | SMDB
SMDB-SF-01
| Run status of CB | 1
| Trip status | 1
1 | Air Handling Unit - Gymnasium
| Supply temperature & humidity |  |  | 2
| Return/Space air temperature |  |  | 1
| Fresh air temperature & humidity |  |  | 2
| Supply fan start/stop command |  | 1
| Supply fan ON/OFF status | 1
| Supply fan trip status | 1
| Supply fan auto position | 1
| Supply fan proof of flow | 1
| Supply fan VFD command & feedback |  |  | 1 | 1
| Dampers open/close status | 1
| Pre & Bag filter dirty status | 1
| Chilled water valve position command & feedback |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
Smoke detection
| Exhaust fan VFD command & feedback |  |  | 1 | 1
| Exhaust fan start/stop command |  | 1
| Exhaust fan ON/OFF status | 1 |  |  |  | 1
| Exhaust fan trip status | 1
| Exhaust fan auto position | 1
| Exhaust fan Proof of flow | 1
| Exhaust temperature & humidity |  |  | 2
| Total Recovery wheel start/stop command |  | 1
| Total Recovery wheel on/off status | 1
| Total Recovery wheel fault status | 1
| Fresh air wheel leaving temperature & humidity |  |  | 2
| Carbon dioxide level - Duct |  |  | 1
| Carbon dioxide level- Space |  |  | 1
| Return Air Temp and Humidity (Duct & wall) |  |  | 4
| Wall mount Thermostat |  |  | 1
| Reheat valve command and feedback |  |  | 1 | 1
2 | Smoke Extract Fan
SEF-RF-15,SEF-RF-16
| Fan run status | 2 |  |  |  | 2
| Fan trip status | 2
| Smoke detector by fire alarm |  |  |  |  | 2
| Fire alarm signal |  |  |  |  | 2
| Fan in AUTO position at MCC | 2
1 | Staircase Pressurization Fan
PF-RF-06
| Smoke detector by fire alarm |  |  |  |  | 1
| Fan start/stop command (By Fire Alarm) |  |  |  |  | 1
| Fan run status | 1 |  |  |  | 1
| Fan trip status | 1
| Fan in Auto position at MCC | 1
2 | Air Curtain - AC-07,08
| Unit normal/fault | 2
| TOTAL | 37 | 6 | 42 | 8 | 11
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-SF-02 (ROOF -Z1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-06
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return air temperature |  |  | 1
| Space temperature |  |  | 1
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Total recovery wheel start/stop command |  | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh/Exhaust air damper open/close status | 1
| Pre & Bag filter dirty status | 1
| Chilled water pressure independent valve control & position |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  |  | 1
| Supply fan control |  | 1 |  | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status | 1
| Exhaust fan control |  | 1 |  | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
1
1 | Smoke Extract Fan
SEF-RF-02
| Fan run status | 1 |  |  |  | 1
| Fan trip status | 1
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 1
1 | Staircase Pressurization Fan
PF-RF-05
| Smoke detector by fire alarm |  |  |  |  | 1
| Fan start/stop command (By Fire Alarm) |  |  |  |  | 1
| Fan run status | 1 |  |  |  | 1
| Fan trip status | 1
| Fan in Auto position at MCC | 1
1 | SMDB
SMDB-SF1
| Run status of CB | 1
| Trip status | 1
1 | Lift-5
| Run status | 1
| Cabin Call Alarm | 1
| Fault Status | 1
| TOTAL | 22 | 3 | 15 | 3 | 5
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-01 (ROOF -Z3PT1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-05 (MCC & Field Side)
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return/Space air temperature |  |  | 2
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Total recovery wheel start/stop command |  | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh/Exhaust air damper open/close status | 1
| Pre&Bag filter dirty status | 1
| Return filter dirty status | 1
| Chilled water pressure independent valve control & position |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  |  | 1
| Supply fan control |  | 1 |  | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status | 1
| Exhaust fan control |  | 1 |  | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-01 (MCC & Field Side)
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return/Space air temperature |  |  | 2
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Total recovery wheel start/stop command |  | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh/Exhaust air damper open/close status | 1
| Pre&Bag filter dirty status | 1
| Return filter dirty status | 1
| Chilled water pressure independent valve control & position |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  |  | 1
| Supply fan control |  | 1 |  | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status | 1
| Exhaust fan control |  | 1 |  | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-02 (MCC Side)
| Total recovery wheel start/stop command |  | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh/Exhaust air damper open/close status | 1
| Supply fan control |  | 1 |  | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status | 1
| Exhaust fan control |  | 1 |  | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
2 | Exhaust Fan
EF-RF-08 (Kitchen & Garbage Room), EF-RF-09 (UPS Room)
| Fan start/stop command |  | 2
| Fan running status | 2 |  |  |  | 2
| Fan trip status | 2
| Fan auto status | 2
1 | SMDB
SMDB-RF1
| Run status of CB | 1
| Trip status | 1
1 | ESMDB
ESMDB-RF1
| Run status of CB | 1
| Trip status | 1
| TOTAL | 41 | 11 | 30 | 8 | 2
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-02 (ROOF -Z2PT1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Smoke Extract Fan
SEF-RF-06
| Fan run status | 1 |  |  |  | 1
| Fan trip status | 1
| Fire alarm signal |  |  |  |  | 3
| Fan in AUTO position at MCC | 1
2 | Exhaust Fan
EF-RF-01 (BIO -LAB) ,EF-RF-02 (HEALTH-SCIENCE LAB )
| Fan start/stop command |  | 2
| Fan run status | 2 |  |  |  | 2
| Fan trip status | 2
| Fan auto status | 2
1 | Smoke Makeup Fan
MAF-RF-06
| Fan run status | 1 |  |  |  | 1
| Fan trip status | 1
| Fire alarm signal |  |  |  |  | 2
| Fan in AUTO position at MCC | 1
1 | Booster Pump (2D/1S)
| Pump ON/OFF status | 3
| Pump trip status | 3
| Pump in auto position status | 3
1 | Hot Water Circulation Pump (1D+1S)
| Pump run status | 2
| Pump trip status | 2
1 | Cold Water Circulation Pump (1D+1S)
| Pump run status | 2
| Pump trip status | 2
1 | CU/AG IONIZER
| on/off status | 1
| fault alarm | 1
1 | UV Sterilization
| Filter dirty status | 1
2 | Water Tank
| Water high & low level status |  |  |  |  | 2
| Tank level |  |  | 2
| TOTAL | 32 | 2 | 2 | 0 | 11
QTY | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-03 (ROOF -Z3PT1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
2 | Smoke Makeup Fan
MAF-RF-01, RF-04
| Fan run status | 2 |  |  |  | 2
| Fan trip status | 2
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 2
2 | Exhaust Fan
EF-RF-03 (CHEM LAB) ,EF-RF-11 (NATURALIZATION ROOM)
| Fan start/stop command |  | 2
| Fan running status | 2 |  |  |  | 2
| Fan trip status | 2
| Fan auto status | 2
1 | Staircase Pressurization Fan
PF-RF-02
| Smoke detector by fire alarm |  |  | 1
| Fan start/stop command (By Fire Alarm) |  |  | 1
| Fan run status | 1 |  |  |  | 1
| Fan trip status | 1
| Fan in Auto position at MCC | 1
2 | Smoke Extract Fan
SEF-RF-01,RF-04
| Fan run status | 2 |  |  |  | 2
| Fan trip status | 2
| Fire alarm signal |  |  |  |  | 2
| Fan in AUTO position at MCC | 2
1 | DX- Air Handling Unit
AHU-RF-01-DX
| Fresh/Return air damper open/close status | 1
| Pre&Bag filter dirty status | 1
| Return filter dirty status | 1
| Supply fan run status | 1 |  |  |  | 1
| Supply fan trip status | 1
| Supply fan HOA status | 1
| Supply fan start/stop command |  | 1
| Supply temperature & humidity |  |  | 2
| Return/Space temperature |  |  | 1
| Supply Fan VFD Command & Feedback |  |  | 1 | 1
| Off coil temperature & humidity |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Smoke Detector |  |  |  |  | 1
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-02 ( Field Side)
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return/Space air temperature |  |  | 2
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Pre&Bag filter dirty status | 1
| Return filter dirty status | 1
| Chilled water pressure independent valve control & position |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  |  | 1
1 | SMDB
SMDB-SF4
| Run status of CB | 1
| Trip status | 1
| TOTAL | 31 | 3 | 25 | 2 | 12
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-04 (ROOF -Z2PT3 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Smoke Extract Fan
SEF-RF-03
| Fan run status | 1 |  |  |  | 1
| Fan trip status | 1
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 1
1 | Smoke Makeup Fan
MAF-RF-03
| Fan run status | 1 |  |  |  | 1
| Fan trip status | 1
| Fire alarm signal |  |  |  |  | 2
| Fan in AUTO position at MCC | 1
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-03 (MCC Side)
| Total recovery wheel start/stop command |  | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh/Exhaust air damper open/close status | 1
| Supply fan control |  | 1 |  | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status | 1
| Exhaust fan control |  | 1 |  | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-04 (MCC Side)
| Total recovery wheel start/stop command |  | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh/Exhaust air damper open/close status | 1
| Supply fan control |  | 1 |  | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status | 1
| Exhaust fan control |  | 1 |  | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
2 | SMDB
SMDB-RF2,SF3
| Run status of CB | 2
| Trip status | 2
1 | ESMDB
ESMDB-RF2
| Run status of CB | 1
| Trip status | 1
1 | Outside Temperature & Humidity Sensor
| Outside Temperature & Humidity Sensor |  |  | 2
| TOTAL | 30 | 6 | 2 | 4 | 5
QTY | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-05 (Z3PT3) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Staircase Pressurization Fan
PF-RF-03
| Smoke detector by fire alarm |  |  |  |  | 1
| Fan start/stop command (By Fire Alarm) |  |  |  |  | 1
| Fan run status | 1 |  |  |  | 1
| Fan trip status | 1
| Fan in OFF position at MCC | 1
4 | Exhaust Fan
EF-RF-05 (GF CAFETERIA ),EF-RF-06 (BIO -LAB), EF-RF-07 (HEALTH - SCIENCE LAB), EF-RF-04 (CHEM LAB)
| Fan start/stop command |  | 4
| Fan running status | 4 |  |  |  | 4
| Fan trip status | 4
| Fan auto status | 4
2 | Smoke Makeup Fan
MAF-RF-07,RF-05
| Fan run status | 2 |  |  |  | 2
| Fan trip status | 2
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 2
2 | Smoke Extract Fan
SEF-RF-07,RF-05
| Fan run status | 2 |  |  |  | 2
| Fan trip status | 2
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 2
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-03 ( Field Side)
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return/Space air temperature |  |  | 2
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Pre&Bag filter dirty status | 1
| Return filter dirty status | 1
| Chilled water pressure independent valve control & position |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  |  | 1
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-04 ( Field Side)
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return/Space air temperature |  |  | 2
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Pre&Bag filter dirty status | 1
| Return filter dirty status | 1
| Chilled water pressure independent valve control & position |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  |  | 1
| TOTAL | 31 | 4 | 30 | 2 | 13
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-SP-01 (SWP PUMP ROOM) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
4 | Filter & Treatment Pumpset
CRP-BNSP2-LG-01,02,03,04
| Pump Run Status | 4
| Pump Trip Status | 4
| Pump Auto Status | 4
2 | UV Sterilization Unit
| Unit run status | 2
1 | Auto Chemical Dosing Unit
| Unit run status | 1
2 | Dosing Unit
| Unit run status | 2
3 | Backwash Filters
| Unit run status | 3
2 | Swimming Pool Booster Pump (1D+1S)
FP-BNSP2-LG-01,02
| Pump Run Status | 2
| Pump Trip Status | 2
| Pump Auto Status | 2
1 | Sump Pump (1D+1S)
| Pump status | 2
| Pump trip status | 2
| Pump in auto position status | 2
| Sump pit high level alarm |  |  |  |  | 1
| Sump pit low level alarm |  |  |  |  | 1
1 | GRP Surge Tank
WT-BNSP2-RF-01
| Water high & low level status |  |  |  |  | 2
| Tank level |  |  | 1
1 | Swimming Pool Underwater Lights
| On/Off Status |  |  |  |  | 1
| TOTAL | 32 | 0 | 1 | 0 | 4
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-SB-01 (SUBSTATION BLDG.) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
2 | DX Unit
IDU-GF-02 (Telecom Room),GF-03 (MV Room)
| Space Temperature |  |  | 2
| Unit enable/disable command |  | 2
| Split unit status | 2
1 | Generator Exhaust Fan
EF-GF-01
| Fan start/stop command |  | 1
| Fan running status | 1 |  |  |  | 1
| Fan trip status | 1
| Fan auto status | 1
1 | Exhaust Fan
EF-GF-02 (SOLID WASTE ROOM)
| Fan start/stop command |  | 1
| Fan running status | 1 |  |  |  | 1
| Fan trip status | 1
| Fan auto status | 1
1 | ATS
| On status of Incomer CB | 1
| Off status of Incomer CB | 1
| By pass position | 1
| Normal fault status | 1
2 | AHU-Cooling Coil
AHU-GF-01, AHU-GF-02-DX
| Supply temperature & humidity |  |  | 4
| Return/Space air temperature |  |  | 4
| Supply damper open/close status | 2
| Pre&Bag filter dirty status | 2
| Return filter dirty status | 2
| Chilled water pressure independent valve control & position |  |  | 2 | 2
| Chilled water return temperature |  |  | 2
| Carbon dioxide level |  |  | 2
| Duct static pressure plus high limit |  |  | 2
| Supply fan control |  | 2 |  | 2
| Supply fan running status | 2
| Supply fan trip | 2
| Supply fan auto status | 2
| Exhaust fan control |  | 2 |  | 2
| Exhaust fan running status | 2
| Exhaust fan trip | 2
| Exhaust fan auto status | 1
| Smoke Detector |  |  |  |  | 2
1 | SMDB
SMDB-LV
| Run status of CB | 1
| Trip status | 1
3 | MDB
MDB-01,02,03
| Main incomer Run status of CB | 3
| Main incomer Trip status of CB | 3
1 | EMDB
SMDB-LV
| Run status of CB | 1
| Trip status | 1
4 | Gate Barrier - 4/1 , 4/2 , 5/1 , 5/2
| Unit on/off status | 4
| TOTAL | 43 | 8 | 18 | 6 | 4
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-LG-01(LOWER GROUND PUMP ROOM) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
3 | GRP Water Tank
| Water high & low level status |  |  |  |  | 3
| Tank level |  |  | 3
4 | RCC Water Tank
| Water high & low level status |  |  |  |  | 4
| Tank level |  |  | 4
2 | Intenal & External Irrigation Pump (1D+1S)
| Pump ON/OFF status | 2
| Pump trip status | 2
| High consumption |  |  |  |  | 2
1 | Transfer Pump (1D+1S)
TRP-BNSP2-LG-01&02
| Pump ON/OFF status | 2
| Pump trip status | 2
| Pump in AUTO position at MCC | 2
1 | Fire Water Circulation Pump (1D+1S)
CRP-BNSP2-LG-01&02
| Pump trip status | 2
| Pump ON/OFF status | 2
| Pump HOA status | 2
2 | Multimedia Filter (2D)
SDF-BNSP2-LG-01&02
| Filter dirty status | 2
1 | Fire Pump (1D+1E+1J)
| Electric pump run status | 1
| Electric pump fault status | 1
| Disel pump run status | 1
| Disel pump fault status | 1
| Jockey pump run status | 1
| Static pressure |  |  | 1
2 | Sump Pump (1D+1S) - 01,02
| Pump run status | 4
| Pump trip status | 4
| Pump Auto Status | 4
| Sump pit high level alarm |  |  |  |  | 2
| Sump pit low level alarm |  |  |  |  | 2
1 | Fire Room Makeup Air Fan
MAF-LG-02
| Motorized damper open/close status |  |  |  |  | 1
| Fan running status | 1 |  |  |  | 1
| Fan trip status | 1
| Fan AUTO status | 1
1 | Fire Room Exhaust Fan
EF-LG-02
| Motorized damper open/close status |  |  |  |  | 1
| Fan running status | 1 |  |  |  | 1
| Fan trip status | 1
| Fan AUTO status | 1
| TOTAL | 41 | 0 | 8 | 0 | 17
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-LG-02(LOWER GROUND PARKING AREA) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | SMDB
SMDB-LG-PB
| Run status of CB | 1
| Trip status | 1
1 | ESMDB
ESMDB-LG-PB
| Run status of CB | 1
| Trip status | 1
1 | DX Unit
IDU-LG-01 (Serving Meter Room)
| Space Temperature |  |  | 1
| Unit enable/disable command |  | 1
| Split unit status | 1
1 | Sump Pump-LG-03 (1D+1S)
| Pump run status | 2
| Pump trip status | 2
| Pump Auto Status | 2
| Sump pit high level alarm |  |  |  |  | 1
| Sump pit low level alarm |  |  |  |  | 1
8 | Jet Fans (JF-LG-19:26)
| Start/Stop Low Speed Command |  | 8
| RUN Status | 8
| Trip Status | 8
| Auto Status | 8
5 | Gate Barrier 6/1 , 6/2 , PB1,PB2,PB3
| Unit on/off status | 5
| TOTAL | 40 | 9 | 1 | 0 | 2
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-LG-03(LOWER GROUND PARKING AREA) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | SMDB
SMDB-EV-PB
| Run status of CB | 1
| Trip status | 1
1 | Sump Pump-LG-02 (1D+1S)
| Pump status | 2
| Pump trip status | 2
| Pump in auto position status | 2
| Sump pit high level alarm |  |  |  |  | 1
| Sump pit low level alarm |  |  |  |  | 1
18 | Jet Fans (JF-LG-1:18)
| Start/Stop Low Speed Command |  | 18
| RUN Status | 18
| Trip Status | 18
| Auto Status | 18
| TOTAL | 62 | 18 | 0 | 0 | 2
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-UG-01(UPPER GROUND PARKING AREA) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
17 | Jet Fans (JF-UG-8,10,12:26)
| Start/Stop Low Speed Command |  | 17
| RUN Status | 17
| Trip Status | 17
| Auto Status | 17
| TOTAL | 51 | 17 | 0 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-UG-02(UPPER GROUND PARKING AREA) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
9 | Jet Fans (JF-UG-1:7,9,11)
| Start/Stop Low Speed Command |  | 9
| RUN Status | 9
| Trip Status | 9
| Auto Status | 9
| TOTAL | 27 | 9 | 0 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| SOFTWARE INTEGRATION | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Chiller Plant Manager
| via Bacnet IP Integration |  |  |  |  | 50
1 | CRAC
| via Bacnet IP Integration |  |  |  |  | 10
402 | FCU Commuicating Modulating
| Bacnet MS/TP Software integration |  |  |  |  | 2814
2 | Fire Alarm Control Panel
via Bacnet IP Integration
| Main Fire Alarm |  |  |  |  | 2
| Zone Wise Alarms |  |  |  |  | 15
| Smoke Detectors |  |  |  |  | 20
| Motorized Smoke Dampers |  |  |  |  | 30
1 | Central Battery System
| via Bacnet IP Integration |  |  |  |  | 20
1 | UPS - Uninterruptible Power Supply
| via Bacnet IP Integration |  |  |  |  | 20
1 | Generator
| via Modbus integration |  |  |  |  | 20
1 | Lighting Control System
| via Bacnet IP Integration |  |  |  |  | 50
1 | AV System
| via Bacnet IP Integration |  |  |  |  | 20
108 | Energy Meter (PMU)
| via Modbus integration |  |  |  |  | 10
31 | Water Meter
| via Modbus integration |  |  |  |  | 10
90 | ACCESS CONTROL
via Bacnet IP Integration
| Fault status |  |  |  |  | 90
| Run Status |  |  |  |  | 90
8 | EV Charging Station
| via IP integration |  |  |  |  | 8
1 | Irrigation System Controller
| via Bacnet IP Integration |  |  |  |  | 10
1 | Dehumidifier
| via Bacnet IP Integration |  |  |  |  | 5
1 | Solar Heating System with Calorifiers
| via Bacnet IP Integration |  |  |  |  | 20
3 | Capacitor Bank
Modbus RS485 Integration
| Breaker Status |  |  |  |  | 3
| Lead and lag power factor |  |  |  |  | 3
| Over voltage |  |  |  |  | 3
| Over current |  |  |  |  | 3
| Over temperature |  |  |  |  | 3
| Frequency |  |  |  |  | 3
10 | NOVEC SYSTEM
via BACNET/IP Integration
| Healthy Status |  |  |  |  | 10
| TOTAL | 0 | 0 | 0 | 0 | 3342
Note on G991: HP: need exact requirement from client for breakdown
Note on G1026: HP: Cannot decided without exact requirement from client
Note on G1027: HP: Cannot decided without exact requirement from client

## Approved
Quantity | LOCATION OF EQUIPMENT | Required Points
| Start From Here | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
| TOTAL (1 System) | 0 | 0 | 0 | 0 | 0
| TOTAL | 0 | 0 | 0 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-GF-01 (ELECTRICAL ROOM Z4PT3) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
3 | Ceiling Air Handling Unit
CAHU-4,5,6
| Supply temperature & humidity |  |  | 6
| Return air temperature |  |  | 3
| Space temperature |  |  | 3
| Carbon dioxide level |  |  | 3
| Supply fan start/stop command |  | 3
| Supply fan ON/OFF status | 3
| Supply fan trip status | 3
| Supply fan proof of flow | 3
| Chilled water valve position command & feedback |  |  | 3 | 3
| Chilled water return temperature |  |  | 3
2 | SMDB
SMDB-GF-MP, SMDB-FF-02
| Run status of CB | 2
| Trip status | 2
1 | Outdoor Pre Insulated Pipe Leak Detection System
| Leak Detection Alarm | 1
1 | ESMDB
ESMDB-GF-MP
| Run status of CB | 1
| Trip status | 1
2026-03-09
| TOTAL | 16 | 3 | 21 | 3 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-GF-02 (EQUIPMENT ROOM - Z4PT1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
3 | Ceiling Air Handling Unit
CAHU-1,2,3
| Supply temperature & humidity |  |  | 6
| Return air temperature |  |  | 3
| Space temperature |  |  | 3
| Carbon dioxide level |  |  | 3
| Supply fan start/stop command |  | 3
| Supply fan ON/OFF status | 3
| Supply fan trip status | 3
| Supply fan proof of flow | 3
| Chilled water valve position command & feedback |  |  | 3 | 3
| Chilled water return temperature |  |  | 3
2 | DX Unit
IDU-GF-04(UPS Room),05 (SEC. Room)
| Space Temperature |  |  | 2
| Unit enable/disable command |  | 2
| Split unit status | 2
2 | CCTV RACK
| Main On/Off status | 2
| UPS On/Off Status | 2
1 | CCTV RACK
| Main On/Off status | 1
| UPS On/Off Status | 1
1 | PAVA System
| Unit on/off status | 1
| Normal/fault status | 1
2 | Novec System
| Unit normal/fault | 2
| TOTAL | 21 | 5 | 23 | 3 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-GF-03 (FCC ROOM - Z1PT2 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | PAVA System
| Unit on/off status | 1
| Normal/fault status | 1
1 | Novec System
| Unit normal/fault | 1
1 | Disabled Toilet Alarm
| Unit on/off status | 1
| Common fault alarm | 1
3 | Gate Barrier - 10,11,12
| Unit on/off status | 3
3 | Gate Barrier - 13,14,15
| Unit on/off status | 3
1 | Access Control Panel
| Power on/off status | 1
5 | Access Control Panel
| Power on/off status | 5
1 | DX Unit
IDU-GF-01 (FCC Room)
| Space Temperature |  |  | 1
| Unit enable/disable command |  | 1
| Split unit status | 1
1 | SMDB
SMDB-EV-EXT
| Run status of CB | 1
| Trip status | 1
2 | Air Curtain
| Unit normal/fault | 2
| TOTAL | 22 | 1 | 1 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-GF-04 (STORAGE ROOM - Z1PT1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | SMDB
SMDB-GF-04
| Run status of CB | 1
| Trip status | 1
1 | ESMDB
ESMDB-GF-4
| Run status of CB | 1
| Trip status | 1
2 | Access Control Panel
| Power on/off status | 2
14 | Access Control Panel
| Power on/off status | 14
3 | Air Curtain
| Unit normal/fault | 3
1 | Lift-4
| Run status | 1
| Cabin Call Alarm | 1
| Fault Status | 1
| TOTAL | 26 | 0 | 0 | 0 | 0
QTY | LOCATION OF EQUIPMENT | Required Points
| DDC-GF-05 (ELECTRICAL ROOM - Z3PT2) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
2 | SMDB
SMDB-FF-01,GF-01
| Run status of CB | 2
| Trip status | 2
2 | Access Control Panel
| Power on/off status | 2
12 | Access Control Panel
| Power on/off status | 12
2 | Novec System
| Unit normal/fault | 2
1 | ESMDB
ESMDB-GF-01
| Run status of CB | 1
| Trip status | 1
1 | USMDB
USMDB-GF-01
| Run status of CB | 1
| Trip status | 1
3 | DX Unit
IDU-GF-06 (UPS Room),07(Telecom Room),08(GSM Room)
| Space Temperature |  |  | 3
| Unit enable/disable command |  | 3
| Split unit status | 3
1 | SERVER ROOM - Leak Detection System
| Leak Detection System | 1
2 | Master Clock System
| Common fault alarm | 2
| Unit on/off status | 2
1 | Lift-1
| Run status | 1
| Cabin Call Alarm | 1
| Fault Status | 1
| TOTAL | 35 | 3 | 3 | 0 | 0
QTY | LOCATION OF EQUIPMENT | Required Points
| DDC-FF-01 (ELECTRICAL ROOM - Z3PT3) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
3 | SMDB
SMDB-FF-02,SF-02,GF-2
| Run status of CB | 3
| Trip status | 3
1 | ESMDB
ESMDB-GF-02
| Run status of CB | 1
| Trip status | 1
2 | Access Control Panel
| Power on/off status | 2
16 | Access Control Panel
| Power on/off status | 16
1 | Lift-2
| Run status | 1
| Cabin Call Alarm | 1
| Fault Status | 1
| TOTAL | 29 | 0 | 0 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-FF-02 (ELECTRICAL ROOM -Z2PT3 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
3 | Air Curtain
| Unit normal/fault | 3
2 | Access Control Panel
| Power on/off status | 2
10 | Access Control Panel
| Power on/off status | 10
2 | SMDB
SMDB-GF-03,FF-03
| Run status of CB | 2
| Trip status | 2
1 | ESMDB
ESMDB-GF-03
| Run status of CB | 1
| Trip status | 1
1 | Lift-3
| Run status | 1
| Cabin Call Alarm | 1
| Fault Status | 1
| TOTAL | 24 | 0 | 0 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-SF-01 (ROOF -Z4 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Air Handling Unit - Swimming Pool (AHU-SF-02)
| Supply temperature & humidity |  |  | 2
| Return air temperature & humidity |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply fan start/stop command |  | 1
| Supply fan ON/OFF status | 1
| Supply fan trip status | 1
| Supply fan auto position | 1
| Supply fan proof of flow | 1
| Supply fan VFD command & feedback |  |  | 1 | 1
| Fresh air damper open/close status | 1
| Return air damper open/close status | 1
| Exhaust air damper open/close status | 1
| Pre filter dirty status | 1
| Bag filter dirty status | 1
| Chilled water valve position command & feedback |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Smoke detection |  |  |  |  | 1
| Exhaust fan VFD command & feedback |  |  | 1 | 1
| Exhaust fan start/stop command |  | 1
| Exhaust fan ON/OFF status | 1
| Exhaust fan trip status | 1
| Exhaust fan auto position | 1
| Exhaust fan Proof of flow | 1
| Exhaust temperature & humidity |  |  | 2
| Total Recovery wheel start/stop command |  | 1
| Total Recovery wheel on/off status | 1
| Total Recovery wheel fault status | 1
| Fresh air wheel leaving temperature & humidity |  |  | 2
| Carbon dioxide level (Duct) 3 nos - multiple return duct branches |  |  | 3
| Carbon dioxide level (Space) 2 nos in hall |  |  | 2
| Return Air Temp and Humidity (Duct & wall) multiple Branches |  |  | 8
| Wall mount Thermostats x 2 for Sace temp plus Set point |  |  | 2
| Reheat valve command and feedback |  |  | 1 | 1
| Return air damper control & position |  |  | 1 | 1
1 | SMDB
SMDB-SF-01
| Run status of CB | 1
| Trip status | 1
1 | Air Handling Unit - Gymnasium
| Supply temperature & humidity |  |  | 2
| Return air temperature & humidity |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply fan start/stop command |  | 1
| Supply fan ON/OFF status | 1
| Supply fan trip status | 1
| Supply fan auto position | 1
| Supply fan proof of flow | 1
| Supply fan VFD command & feedback |  |  | 1 | 1
| Fresh air damper open/close status | 1
| Return air damper open/close status | 1
| Exhaust air damper open/close status | 1
| Pre filter dirty status | 1
| Bag filter dirty status | 1
| Chilled water valve position command & feedback |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Smoke detection |  |  |  |  | 1
| Exhaust fan VFD command & feedback |  |  | 1 | 1
| Exhaust fan start/stop command |  | 1
| Exhaust fan ON/OFF status | 1
| Exhaust fan trip status | 1
| Exhaust fan auto position | 1
| Exhaust fan Proof of flow | 1
| Exhaust temperature & humidity |  |  | 2
| Total Recovery wheel start/stop command |  | 1
| Total Recovery wheel on/off status | 1
| Total Recovery wheel fault status | 1
| Fresh air wheel leaving temperature & humidity |  |  | 2
| Carbon dioxide level (Duct) 3 nos - multiple return duct branches |  |  | 3
| Carbon dioxide level (Space) 2 nos in hall |  |  | 2
| Return Air Temp and Humidity (Duct & wall) multiple Branches |  |  | 8
| Wall mount Thermostats x 2 for Sace temp plus Set point |  |  | 2
| Reheat valve command and feedback |  |  | 1 | 1
| Return air damper control & position |  |  | 1 | 1
2 | Smoke Extract Fan
SEF-RF-15,SEF-RF-16
| Fan ON/OFF status | 2
| Fan trip status | 2
| Proof of flow | 2
| Smoke detector by fire alarm |  |  |  |  | 2
| Fire alarm signal |  |  |  |  | 2
| Fan in AUTO position at MCC | 2
1 | Staircase Pressurization Fan
PF-RF-06
| Smoke detector by fire alarm |  |  |  |  | 1
| Fan start/stop command (By Fire Alarm) |  |  |  |  | 1
| Fan run status | 1
| Fan trip status | 1
| Fan in OFF position at MCC | 1
| TOTAL | 43 | 6 | 62 | 10 | 8
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-SF-02 (ROOF -Z1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-06
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return air temperature & humidity |  |  | 2
| Space temperature |  |  | 1
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Total recovery wheel start/stop command |  | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh air damper open/close status | 1
| Exhaust air damper open/close status | 1
| Pre filter dirty status | 1
| Bag filter dirty status | 1
| Chilled water pressure independent valve control & position |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  |  | 1
| Supply fan control |  | 1 |  | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status | 1
| Exhaust fan control |  | 1 |  | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
1
1 | Smoke Extract Fan
SEF-RF-02
| Fan ON/OFF status | 1
| Fan trip status | 1
| Proof of flow | 1
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 1
1 | Staircase Pressurization Fan
PF-RF-05
| Smoke detector by fire alarm |  |  |  |  | 1
| Fan start/stop command (By Fire Alarm) |  |  |  |  | 1
| Fan run status | 1
| Fan trip status | 1
| Fan in OFF position at MCC | 1
1 | SMDB
SMDB-SF1
| Run status of CB | 1
| Trip status | 1
1 | Lift-5
| Run status | 1
| Cabin Call Alarm | 1
| Fault Status | 1
| TOTAL | 25 | 3 | 16 | 3 | 3
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-01 (ROOF -Z3PT1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-05
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return air temperature & humidity |  |  | 2
| Space temperature |  |  | 1
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Total recovery wheel start/stop command |  | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh air damper open/close status | 1
| Exhaust air damper open/close status | 1
| Pre filter dirty status | 1
| Return filter dirty status | 1
| Chilled water pressure independent valve control & position |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  |  | 1
| Supply fan control |  | 1 |  | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status | 1
| Exhaust fan control |  | 1 |  | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
2 | Exhaust Fan
EF-RF-08 (Kitchen & Garbage Room), EF-RF-09 (UPS Room)
| Fan start/stop command |  | 2
| Fan running status | 2
| Fan trip status | 2
| Fan auto status | 2
1 | Swimming Pool Room Exhaust Fan
EF-LG-01
| Fan start/stop command |  | 1
| Fan running status | 1
| Fan trip status | 1
| Fan auto status | 1
2 | Heat Pumps (1D+1S)
HP-BNSP2-RF-01,02
| Pump run status | 4
| Pump trip status | 4
1 | Pressurization Unit with Feeder Tank (1D + 1S)
| Pump run status | 2
| Pump trip status | 2
| Line Pressure |  |  | 1
| TOTAL | 33 | 6 | 17 | 3 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-02 (ROOF -Z2PT1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
3 | Smoke Extract Fan
SEF-RF-06,RF-04,RF-01
| Fan ON/OFF status | 3
| Fan trip status | 3
| Proof of flow | 3
| Fire alarm signal |  |  |  |  | 3
| Fan in AUTO position at MCC | 3
4 | Exhaust Fan
EF-RF-01 (BIO -LAB) ,EF-RF-02 (HEALTH-SCIENCE LAB ), EF-RF-03 (CHEM LAB) ,EF-RF-11 (NATURALIZATION ROOM)
| Fan start/stop command |  | 4
| Fan running status | 4
| Fan trip status | 4
| Fan auto status | 4
2 | Smoke Makeup Fan
MAF-RF-04,RF-01
| Fan on/off status | 2
| Fan trip status | 2
| Proof of flow | 2
| Fire alarm signal |  |  |  |  | 2
| Fan in AUTO position at MCC | 2
2 | Air Handling Unit with Heat Recovery
HRAHU-RF-01,RF-02
| Fresh air leaving wheel temp & RH |  |  | 4
| Fresh air temperature & humidity |  |  | 4
| Supply temperature & humidity |  |  | 4
| Return air temperature & humidity |  |  | 4
| Space temperature |  |  | 2
| Exhaust temperature & humidity |  |  | 4
| Fresh air flow |  |  | 2
| Total recovery wheel start/stop command |  | 2
| Total recovery wheel on/off status | 2
| Total recovery wheel fault status | 2
| Fresh air damper open/close status | 2
| Exhaust air damper open/close status | 2
| Pre filter dirty status | 2
| Return filter dirty status | 2
| Chilled water pressure independent valve control & position |  |  | 2 | 2
| Chilled water return temperature |  |  | 2
| Carbon dioxide level |  |  | 2
| Duct static pressure plus high limit |  |  | 2
| Supply fan control |  | 2 |  | 2
| Supply fan running status | 2
| Supply fan trip | 2
| Supply fan auto status | 2
| Exhaust fan Control |  | 2 |  | 2
| Exhaust fan running status | 2
| Exhaust fan auto status | 2
| Exhaust fan trip | 2
1 | DX- Air Handling Unit
AHU-RF-01-DX
| Fresh air damper open/close status | 1
| Return air damper open/close status | 1
| Pre filter dirty status | 1
| Bag filter dirty status | 1
| Supply fan run status | 1
| Supply fan trip status | 1
| Supply fan HOA status | 1
| Supply fan start/stop command |  | 1
| Supply temperature & humidity |  |  | 2
| Return temperature & humidity |  |  | 2
| CU start/stop command |  | 1
| CU Run Status | 1
| Off coil temperature |  |  | 1
| Fresh air temperature & humidity |  |  | 2
| Space temperature |  |  | 1
| Smoke Detector |  |  |  |  | 1
1 | Novec System
| Unit normal/fault | 1
1 | SMDB
SMDB-SF4
| Run status of CB | 1
| Trip status | 1
1 | Staircase Pressurization Fan
PF-RF-02
| Smoke detector by fire alarm |  |  | 1
| Fan start/stop command (By Fire Alarm) |  |  | 1
| Fan run status | 1
| Fan trip status | 1
| Fan in OFF position at MCC | 1
| TOTAL | 70 | 12 | 42 | 6 | 6
QTY | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-03 (ROOF -Z3PT1 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | SMDB
SMDB-RF1
| Run status of CB | 1
| Trip status | 1
1 | ESMDB
ESMDB-RF1
| Run status of CB | 1
| Trip status | 1
1 | Novec System
| Unit normal/fault | 1
2 | Access Control Panel
| Power on/off status | 2
4 | Access Control Panel
| Power on/off status | 4
1 | Booster Pump (2D/1S)
| Pump enable/disable command |  | 3
| Pump ON/OFF status | 3
| Pump trip status | 3
| Pump in auto position status | 3
| Pump VFD speed display |  |  |  |  | 3
| Pump VFD trip status |  |  |  |  | 3
| Pump VFD status |  |  |  |  | 3
| Pump VFD speed control |  |  |  |  | 3
| Water volume |  |  |  |  | 1
| High consumption alarm |  |  |  |  | 1
1 | Hot Water Circulation Pump (1D+1S)
| Pump start/stop command |  | 2
| Pump run status | 2
| Pump trip status | 2
1 | Cold Water Circulation Pump (1D+1S)
| Pump start/stop command |  | 2
| Pump run status | 2
| Pump trip status | 2
1 | Copper Silver Ionizer
| Unit on/off status | 1
| Common fault alarm | 1
1 | UV Sterilization
| Filter dirty status | 1
1 | Smoke Makeup Fan
MAF-RF-06
| Fan on/off status | 1
| Fan trip status | 1
| Proof of flow | 1
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 1
1 | Chemical Dosing Unit
| Unit on/off status | 1
| Common fault alarm | 1
2 | Water Tank
| Water high & low level status |  |  |  |  | 2
| Tank level |  |  | 2
1 | Access Control Panel - SF
| Power on/off status | 1
4 | Access Control Panel - SF
| Power on/off status | 4
| TOTAL | 42 | 7 | 2 | 0 | 17
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-04 (ROOF -Z2PT3 ) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
2 | Smoke Extract Fan
SEF-RF-05,RF-03
| Fan ON/OFF status | 2
| Fan trip status | 2
| Proof of flow | 2
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 2
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-03
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return air temperature & humidity |  |  | 2
| Space temperature |  |  | 1
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Total recovery wheel start/stop command |  | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh air damper open/close status | 1
| Exhaust air damper open/close status | 1
| Pre filter dirty status | 1
| Return filter dirty status | 1
| Chilled water pressure independent valve control & position |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  |  | 1
| Supply fan control |  | 1 |  | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status | 1
| Exhaust fan control |  | 1 |  | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
1
1 | Exhaust Fan
EF-RF-04 (CHEM LAB)
| Fan start/stop command |  | 1
| Fan running status | 1
| Fan trip status | 1
| Fan auto status | 1
2 | Smoke Makeup Fan
MAF-RF-05,RF-03
| Fan on/off status | 2
| Fan trip status | 2
| Proof of flow | 2
| Fire alarm signal |  |  |  |  | 2
| Fan in AUTO position at MCC | 2
2 | SMDB
SMDB-RF2,SF3
| Run status of CB | 2
| Trip status | 2
1 | ESMDB
ESMDB-RF2
| Run status of CB | 1
| Trip status | 1
1 | Novec System
| Unit normal/fault | 1
1 | Outside Temperature & Humidity Sensor
| Outside Temperature & Humidity Sensor |  |  | 2
7 | Access Control Panel - SF
| Power on/off status | 1
| TOTAL | 40 | 4 | 18 | 3 | 3
QTY | LOCATION OF EQUIPMENT | Required Points
| DDC-RF-05 (Z3PT3) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Staircase Pressurization Fan
PF-RF-03
| Smoke detector by fire alarm |  |  |  |  | 1
| Fan start/stop command (By Fire Alarm) |  |  |  |  | 1
| Fan run status | 1
| Fan trip status | 1
| Fan in OFF position at MCC | 1
3 | Exhaust Fan
EF-RF-05 (GF CAFETERIA ),EF-RF-06 (BIO -LAB), EF-RF-07 (HEALTH - SCIENCE LAB)
| Fan start/stop command |  | 3
| Fan running status | 3
| Fan trip status | 3
| Fan auto status | 3
1 | Smoke Makeup Fan
MAF-RF-07
| Fan on/off status | 1
| Fan trip status | 1
| Proof of flow | 1
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 1
1 | Smoke Extract Fan
SEF-RF-07
| Fan ON/OFF status | 1
| Fan trip status | 1
| Proof of flow | 1
| Fire alarm signal |  |  |  |  | 1
| Fan in AUTO position at MCC | 1
1 | Air Handling Unit with Heat Recovery
HRAHU-RF-04
| Fresh air leaving wheel temp & RH |  |  | 2
| Fresh air temperature & humidity |  |  | 2
| Supply temperature & humidity |  |  | 2
| Return air temperature & humidity |  |  | 2
| Space temperature |  |  | 1
| Exhaust temperature & humidity |  |  | 2
| Fresh air flow |  |  | 1
| Return air leaving SW temp & RH |  | 1
| Total recovery wheel start/stop command | 1
| Total recovery wheel on/off status | 1
| Total recovery wheel fault status | 1
| Fresh air damper open/close status | 1
| Exhaust air damper open/close status | 1
| Pre filter dirty status | 1
| Return filter dirty status |  |  | 1 | 1
| Chilled water pressure independent valve control & position |  |  | 1
| Chilled water return temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Duct static pressure plus high limit |  | 1 |  | 1
| Supply fan control | 1
| Supply fan running status | 1
| Supply fan trip | 1
| Supply fan auto status |  | 1 |  | 1
| Exhaust fan control | 1
| Exhaust fan running status | 1
| Exhaust fan trip | 1
| Exhaust fan auto status | 1
| TOTAL | 33 | 6 | 16 | 3 | 4
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-SP-01 (SWP PUMP ROOM) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Filter & Treatment Unit
CRP-BNSP2-LG-01
| Automatic screen filter | 1
| Strainer status | 1
| Filterlizer tank low level | 1
| Fertilizer unit status | 1
| Fertilizer unit fault alarm | 1
1 | UV Sterilization
| Filter dirty status | 1
1 | Chemical Dosing Unit
| Unit run status | 1
| Unit fault alarm | 1
3 | Sand Filter (3D)
| Filter dirty status | 3
1 | Swimming Pool Circulation Pump (2D+1S)
FP-BNSP2-LG-01,02,03
| Pump start/stop command |  | 3
| Pump trip status | 3
| Pump running status | 3
| Pump Auto status | 3
1 | Sump Pump (1D+1S)
| Pump status | 2
| Pump trip status | 2
| Pump in auto position status | 2
| Sump pit high level alarm |  |  |  |  | 1
| Sump pit low level alarm |  |  |  |  | 1
1 | GRP Surge Tank
WT-BNSP2-RF-01
| Water high & low level status |  |  |  |  | 2
| Tank level |  |  | 1
| TOTAL | 26 | 3 | 1 | 0 | 4
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-SB-01 (SUBSTATION BLDG.) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
2 | DX Unit
IDU-GF-02 (Telecom Room),GF-03 (MV Room)
| Space Temperature |  |  | 2
| Unit enable/disable command |  | 2
| Split unit status | 2
1 | Generator Exhaust Fan
EF-GF-01
| Fan start/stop command |  | 1
| Fan running status | 1
| Fan trip status | 1
| Fan auto status | 1
1 | Exhaust Fan
EF-GF-02 (OLID WASTE ROOM)
| Fan start/stop command |  | 1
| Fan running status | 1
| Fan trip status | 1
| Fan auto status | 1
1 | Access Control Panel
| Power on/off status | 1
1 | ATS
| On status of Incomer CB | 1
| Off status of Incomer CB | 1
| By pass position | 1
| Normal fault status | 1
1 | AHU-Cooling Coil
AHU-GF-01
| Supply temperature & humidity |  |  | 2
| Return air temperature |  |  | 1
| Fresh air temperature & humidity |  |  | 2
| Space temperature |  |  | 1
| Carbon dioxide level |  |  | 1
| Supply fan start/stop command |  | 1
| Supply fan Auto status | 1
| Supply fan ON/OFF status | 1
| Supply fan trip status | 1
| Supply fan proof of flow | 1
| Supply fan VFD Feedback |  |  | 1
| Supply fan VFD control |  |  |  | 1
| Fresh air damper open/close status |  |  | 1
| Return air damper open/close status |  |  | 1
| Pre filter dirty status | 1
| Bag filter dirty status | 1
| Chilled water valve position command & feedback |  |  | 1 | 1
| Chilled water return temperature |  |  | 1
| Exhaust fan start/stop command |  | 1
| Exhaust fan Auto status | 1
| Exhaust fan ON/OFF status | 1
| Exhaust fan proof of flow | 1
| Exhaust fan trip status | 1
| Exhaust temperature & humidity |  |  | 2
| Total Recovery wheel start/stop command |  | 1
| Total Recovery wheel auto status | 1
| Total Recovery wheel on/off status | 1
| Total Recovery wheel fault status | 1
| Fresh air wheel leaving temperature & humidity |  |  | 2
| Smoke Detector |  |  |  |  | 1
1 | DX- Air Handling Unit
AHU-GF-01-DX
| Fresh air damper open/close status | 1
| Return air damper open/close status | 1
| Pre filter dirty status | 1
| Bag filter dirty status | 1
| Supply fan run status | 1
| Supply fan trip status | 1
| Supply fan HOA status | 1
| Supply fan start/stop command |  | 1
| Supply temperature & humidity |  |  | 2
| CU start/stop status & command |  | 1
| CU Run Status | 1
| Off coil temperature |  |  | 1
| Fresh air temperature & humidity |  |  | 2
| Space temperature |  |  | 1
| Smoke Detector |  |  |  |  | 1
1 | SMDB
SMDB-LV
| Run status of CB | 1
| Trip status | 1
2 | Novec System
| Unit normal/fault | 2
3 | MDB
MDB-01,02,03
| Main incomer Run status of CB | 3
| Main incomer Trip status of CB | 3
1 | EMDB
SMDB-LV
| Run status of CB | 1
| Trip status | 1
8 | Gate Barrier-2,3,4,5,6,7,8,9
| Unit on/off status | 8
| TOTAL | 54 | 9 | 24 | 2 | 2
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-LG-01(LOWER GROUND PUMP ROOM) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
3 | GRP Water Tank
| Water high & low level status |  |  |  |  | 3
| Tank level |  |  | 3
4 | RCC Water Tank
| Water high & low level status |  |  |  |  | 4
| Tank level |  |  | 4
2 | Intenal & External Irrigation Pump (1D+1S)
| Pump enable/disable command |  | 4
| Pump ON/OFF status | 4
| Pump trip status | 4
| High consumption |  |  |  |  | 2
1 | Transfer Pump (1D+1S)
TRP-BNSP2-LG-01&02
| Pump start/stop command |  | 2
| Pump ON/OFF status | 2
| Pump trip status | 2
| Pump in AUTO position at MCC | 2
1 | Fire Water Circulation Pump (1D+1S)
CRP-BNSP2-LG-01&02
| Pump trip status | 2
| Pump ON/OFF status | 2
| Pump HOA status | 2
| Pump start/stop command |  | 2
2 | Multimedia Filter (2D)
SDF-BNSP2-LG-01&02
| Filter dirty status | 2
1 | Fire Pump (1D+1E+1J)
| Electric pump run status | 1
| Electric pump fault status | 1
| Disel pump run status | 1
| Disel pump fault status | 1
| Jockey pump run status | 1
| Static pressure |  |  | 1
2 | Sump Pump (1D+1S) - 01,02
| Pump run status | 4
| Pump trip status | 4
| Pump Auto Status | 4
| Sump pit high level alarm |  |  |  |  | 2
| Sump pit low level alarm |  |  |  |  | 2
1 | Fire Room Makeup Air Fan
MAF-LG-02
| Motorized damper open/close status |  |  |  |  | 1
| Fan running status | 1
| Fan trip status | 1
| Fan AUTO status | 1
1 | Fire Room Exhaust Fan
EF-LG-02
| Motorized damper open/close status |  |  |  |  | 1
| Fan running status | 1
| Fan trip status | 1
| Fan AUTO status | 1
| TOTAL | 45 | 8 | 8 | 0 | 15
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-LG-02(LOWER GROUND PARKING AREA) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | SMDB
SMDB-LG-PB
| Run status of CB | 1
| Trip status | 1
1 | ESMDB
ESMDB-LG-PB
| Run status of CB | 1
| Trip status | 1
1 | Novec System
| Unit normal/fault | 1
1 | DX Unit
IDU-LG-01 (Serving Meter Room)
| Space Temperature |  |  | 1
| Unit enable/disable command |  | 1
| Split unit status | 1
1 | Sump Pump (1D+1S) - 03
| Pump run status | 2
| Pump trip status | 2
| Pump Auto Status | 2
| Sump pit high level alarm |  |  |  |  | 1
| Sump pit low level alarm |  |  |  |  | 1
1 | Sand Trap/Interceptor
SI-BNSP2-LG-01
| Common fault alarm | 1
1 | Access Control Panel
| Power on/off status | 1
1 | Sump Pump (1D+1S)
| Pump status | 2
| Pump trip status | 2
| Pump in auto position status | 2
| Sump pit high level alarm |  |  |  |  | 1
| Sump pit low level alarm |  |  |  |  | 1
26 | Jet Fans
| Start/Stop Low Speed Command |  | 26
| RUN Status | 26
| Trip Status | 26
| Auto Status | 26
| Carbon Monoxide |  |  | 8
| Nitrogen Dioxide |  |  | 8
| Fan Auto Status | 26
1 | Access Control Panel
| Power on/off status | 1
1 | Gate Barrier-1
| Unit on/off status | 1
| TOTAL | 126 | 27 | 17 | 0 | 4
Qty | LOCATION OF EQUIPMENT | Required Points
| DDC-UG-01(UPPER GROUND PARKING AREA) | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Access Control Panel
| Common fault alarm | 1
2 | Access Control Panel
| Power on/off status | 1
26 | Jet Fans
| Start/Stop Low Speed Command |  | 26
| RUN Status | 26
| Trip Status | 26
| Auto Status | 26
| Carbon Monoxide |  |  | 8
| Nitrogen Dioxide |  |  | 8
| TOTAL | 80 | 26 | 16 | 0 | 0
Qty | LOCATION OF EQUIPMENT | Required Points
| SOFTWARE INTEGRATION | DI-Hardware/Software | DO-Hardware/Software | AI-Hardware/Software | AO-Hardware/Software | Integration Points
1 | Chiller Plant Manager
| via Bacnet IP Integration |  |  |  |  | 50
1 | CRAC
| via Bacnet IP Integration |  |  |  |  | 10
402 | FCU Commuicating Modulating
| Bacnet MS/TP Software integration |  |  |  |  | 2814
2 | Fire Alarm Control Panel
| via Bacnet IP Integration |  |  |  |  | 75
1 | Central Battery System
| via Bacnet IP Integration |  |  |  |  | 20
1 | UPS - Uninterruptible Power Supply
| via Bacnet IP Integration |  |  |  |  | 20
1 | Generator
| via Modbus integration |  |  |  |  | 20
1 | Lighting Control System
| via Bacnet IP Integration |  |  |  |  | 50
1 | AV System
| via Bacnet IP Integration |  |  |  |  | 20
108 | Energy Meter (PMU)
| via Modbus integration |  |  |  |  | 10
31 | Water Meter
| via Modbus integration |  |  |  |  | 10
1 | ACCESS CONTROL
| via Bacnet IP Integration |  |  |  |  | 20
8 | EV Charging Station
| via IP integration |  |  |  |  | 8
1 | Irrigation System Controller
| via Bacnet IP Integration |  |  |  |  | 10
1 | Swimming Pool System
via Bacnet IP Integration
| Filter Pump-1 Run Status |  |  |  |  | 1
| Filter Pump-1 Trip Status |  |  |  |  | 1
| Filter Pump-1 Auto Status |  |  |  |  | 1
| Filter Pump-2 Run Status |  |  |  |  | 1
| Filter Pump-2 Trip Status |  |  |  |  | 1
| Filter Pump-2 Auto Status |  |  |  |  | 1
| Filter Pump-3 Run Status |  |  |  |  | 1
| Filter Pump-3 Trip Status |  |  |  |  | 1
| Filter Pump-3 Auto Status |  |  |  |  | 1
| Filter Pump-4 Run Status |  |  |  |  | 1
| Filter Pump-4 Trip Status |  |  |  |  | 1
| Filter Pump-4 Auto Status |  |  |  |  | 1
| Booster Pump-1 Run Status |  |  |  |  | 1
| Booster Pump-1 Trip Status |  |  |  |  | 1
| Booster Pump-1 Auto Status |  |  |  |  | 1
| Booster Pump-2 Run Status |  |  |  |  | 1
| Booster Pump-2 Trip Status |  |  |  |  | 1
| Booster Pump-2 Auto Status |  |  |  |  | 1
| Auto Chemical Dosing Unit On Status |  |  |  |  | 1
| Backwash Unit-1 On Status |  |  |  |  | 1
| Backwash Unit-2 On Status |  |  |  |  | 1
| Backwash Unit-3 On Status |  |  |  |  | 1
| UV Sterilizer-1 On Status |  |  |  |  | 1
| UV Sterilizer-2 On Status |  |  |  |  | 1
| Dosing Unit-1 On Status |  |  |  |  | 1
| Dosing Unit-2 On Status |  |  |  |  | 1
| Swimming Pool Underwater Lights On Status |  |  |  |  | 1
1 | Dehumidifier
| via Bacnet IP Integration |  |  |  |  | 5
1 | Solar Heating System with Calorifiers
| via Bacnet IP Integration |  |  |  |  | 20
3 | Capacitor Bank
Modbus RS485 Integration
| Breaker Status |  |  |  |  | 3
| Lead and lag power factor |  |  |  |  | 3
| Over voltage |  |  |  |  | 3
| Over current |  |  |  |  | 3
| Over temperature |  |  |  |  | 3
| Frequency |  |  |  |  | 3
| TOTAL | 0 | 0 | 0 | 0 | 3207
Note on G1142: HP: need exact requirement from client for breakdown
Note on G1174: HP: Cannot decided without exact requirement from client